## Executive Summary
Fractional Forge Engineering Dossier — Water treatment
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · MIRROR of the dossier floor (min of every deterministic section & non-mirror tab) — re-stamped from the CURRENT scores, never a stale earlier cap; own content check: cov… · full audit: Quality & Audit tab
The engineering reality of your hardware idea — a buildable design, a real bill of materials, the true cost, and who can make it. The detail is in the tabs; this page is the summary.
WHAT IT IS
Water treatment
OUTPUT
90 m³/h
Irrigation Demand delivered · serves 6,000 Cultivation Containers Count
ALL-IN INSTALLED COST
£1,375,105
STATUS
SHIPS
One verdict for the whole dossier — the floor is the minimum score of every section and tab; it ships when all are ≥8. Detail: Quality & Audit tab.
This dossier specifies a Water treatment — 90 m³/h (irrigation demand delivered), serving 6,000 cultivation containers count. The engine values the build at £1,375,105 (all-in installed cost). An independent market benchmark flags 1 dimension where the design diverges from the brief/market expectation — see the ⚠ Checks tab for the routed detail. Every figure in this workbook — the bill of materials, the costs, and the specifications below — is derived deterministically from the engineering contract, computed rather than estimated by hand.
Key specifications & brief compliance — every target deterministically verified
Brief metric | Target | Unit | Matched contract quantity | Achieved | Direction | STATUS | Note | Cell check
Cultivation containers count | 6000 | count | Cultivation container count | 6000 | ≥ target (meet/exceed) | PASS | brief key: cultivation_containers_count → contract: cultivation_container_count · unit family: count | PASS
Water storage capacity m3 | 120 | m3 | Water storage capacity m3 | 120 | ≥ target (meet/exceed) | PASS | brief key: water_storage_capacity_m3 → contract: water_storage_capacity_m3 · unit family: volume_m3 | PASS
Actuated valves count | 200 | count | Actuated distribution valve count | 200 | ≥ target (meet/exceed) | PASS | brief key: actuated_valves_count → contract: actuated_distribution_valve_count · unit family: count | PASS
Irrigation demand (m³/h) | 45 | m3/h | Irrigation pump flow (m³/h) | 90 | ≥ target (meet/exceed) | PASS | brief key: irrigation_demand_m3_per_hr → contract: irrigation_pump_flow_m3_h · unit family: flow_m3h | PASS
Ro permeate capacity (m³/h) | 8 | m3/h | Ro permeate capacity (m³/h) | 8 | ≥ target (meet/exceed) | PASS | brief key: ro_permeate_capacity_m3_per_hr → contract: ro_permeate_capacity_m3_h · unit family: flow_m3h | PASS
Hand watering capacity (m³/h) | 25 | m3/h | Hand watering pump throughput (m³/h) | 25 | ≥ target (meet/exceed) | PASS | brief key: hand_watering_capacity_m3_per_hr → contract: hand_watering_pump_throughput_m3_h · unit family: flow_m3h | PASS
Ro recovery (%) | 75 | % | Ro recovery (%) | 75 | ≥ target (meet/exceed) | PASS | brief key: ro_recovery_percent → contract: ro_recovery_percent | PASS
Where the money goes — capex by category
Pipework & valves | 339642 |  | 42 | █████████████████
Filtration & membranes | 126172 |  | 15.6 | ██████
Vessels, tanks & columns | 107774 |  | 13.3 | █████
Controls & instrumentation | 93229 |  | 11.5 | █████
Other equipment | 65693 |  | 8.1 | ███
Rotating equipment | 35295 |  | 4.4 | ██
Power & electrical | 30736 |  | 3.8 | ██
What's inside this workbook
• Bill of Materials (Ledger) | The bill — tag, item, qty, unit £, cost basis, spec.
• Cost waterfall | Bill of materials to installed price, with live running totals.
• Financial model | Economics, scenarios and investment analysis, live off the Inputs tab.
• Calculations | Worked calculations by tool — live Excel formulas where structured.
• Risk & Regulatory | Hazard and risk register, compliance verdict and statutory duties.
• Connection trace | Which part connects to what, with live cell references.
Your next steps — from design to a funded factory
• You have the engineering dossier
A buildable design, a real bill of materials, and the true cost — this document.
→ Talk to the experts this design needs
We connect you to vetted specialists for the open questions the design raises.
→ Get real supplier quotes (RFQ)
We take this bill of materials to suppliers and bring back real quotes.
→ Raise the money on these numbers
We help you turn the validated design and costs into a fundraise.
Fractional Forge — Tristan Fischer, Founder. Reply to take the next step.

## Contents
Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · index integrity (both directions) — index rows point at an existing tab 30/30; every sheet listed in the index 30/30; cell completeness+type contract 90/90 · score = min… · full audit: Quality & Audit tab
Click any tab name to jump to it. Each data tab has a '↑ Contents' link at its top-right to come back. Yellow cells anywhere are editable inputs; green cells are live formulas.
# | Tab | What's on it | Cell check
1 | Executive Summary | The cover — what it is, cost, verdict and next steps. | PASS
2 | Overview | Run provenance, quality scorecard and headline metrics. | PASS
3 | Renders | Photoreal render gallery — interior hero, plan and exterior views. | PASS
4 | Cost waterfall | Bill of materials to installed price, with live running totals. | PASS
5 | Financial model | Economics, scenarios and investment analysis, live off the Inputs tab. | PASS
6 | Bill of Materials (Ledger) | The bill — tag, item, qty, unit £, cost basis, spec. | PASS
7 | Brief | Original client brief and the engine's structured interpretation. | PASS
8 | Design basis | Codes, design duties, fluid and utilisation basis — with sources. | PASS
9 | Drawings | Drawing register — number, revision, scale, sheets and full-size A1 files. | PASS
10 | BFD — Block Flow | Block flow diagram — major process blocks & streams. | PASS
11 | P&ID | Piping & instrumentation diagram — process flow, valves, instruments. | PASS
12 | Process schedules | Valve and instrument schedules; the line list is Line & velocity. | PASS
13 | GA — General Arrangement | General arrangement — equipment layout & footprint. | PASS
14 | HVAC | Ventilation & climate-control schematic. | PASS
15 | Electrical | Single-line diagram with the panel/load schedule — one dataset. | PASS
16 | Line & velocity | THE line list — every sized run versus its limit. | PASS
17 | Assembly sequence | Order of works from civils through to commissioning. | PASS
18 | Risk & Regulatory | Hazard and risk register, compliance verdict and statutory duties. | PASS
19 | Holds & exclusions | Numbered open holds derived live from failing checks; scope exclusions. | PASS
20 | Questions for the customer | Numbered confirm-or-correct questions — assumptions, gaps and offer divergences. | PASS
21 | Quality & Audit | Sections, per-tab scores and audit findings — one verdict. | PASS
22 | Sense-check | Independent market benchmark versus the engine's numbers. | PASS
23 | ⚠ Checks | Live arithmetic invariants — red rows show numbers that don't reconcile. | PASS
24 | Connection trace | Which part connects to what, with live cell references. | PASS
25 | Quantities | Every sized contract quantity with family, basis and source. | PASS
26 | Calculations | Worked calculations by tool — live Excel formulas where structured. | PASS
27 | Inputs & Assumptions | Editable yellow drivers feeding the economics model. | PASS
28 | Part names | Master parts list; every other tab references these cells. | PASS
29 | Glossary | Plain-English meaning of every abbreviation in the workbook. | PASS
30 | Audit data | Embedded operands every live verdict formula references, with provenance. | PASS

## Overview
Fractional Forge Design Dossier — water-treatment-example |  |  |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · dashboard integrity (every quoted number vs its engine source) — capex category % = 100 × £ / Σ (per-row arithmetic) 10/10; Σ capex categories ≈ the BoM materials total … · full audit: Quality & Audit tab
Live Excel review surface. Yellow cells are editable inputs; green cells are live formulas that recompute downstream. See the '⚠ Checks' tab for invariants that go RED where the engine's numbers do not reconcile.
Run provenance
Run directory | water-treatment-example
Git short SHA | 7099fa8c7
State saved at | 2026-07-04T04:18:38.909Z
Project id | chain-v2-1783138718909
Product class | water_treatment
Quality scorecard
VERDICT: SHIPS · floor 8/10 (min of every DETERMINISTIC section & non-mirror tab — live cells on Quality & Audit; the LLM self-audit is advisory and never floors; ships at ≥8 everywhere)
No quality-scorecard found.
Computational checks
Deterministic invariants | 103 / 103 pass · 0 FAIL | full detail on the ⚠ Checks tab
Headline metrics
Metric | Value | Unit | Notes / source | Cell check
Irrigation Demand delivered | 90 | m³/h | the plant's boundary deliverable (derived from contract quantity 'irrigation_demand_m3_h'); the brief's '6,000 Cultivation Containers Count' is the served-asset demand it MEETS — shown as context | PASS
Unit cost ceiling | 1,400,000 | GBP | Brief cost ceiling per unit. | PASS
Water Storage Capacity | 120 | m3 | Brief target metric (scale). | PASS
Actuated Valves Count | 200 | count | Brief target metric (scale). | PASS
Irrigation Demand M3 Per | 45 | m3/h | Brief target metric (performance). | PASS
Ro Permeate Capacity M3 Per | 8 | m3/h | Brief target metric (performance). | PASS
Hand Watering Capacity M3 Per | 25 | m3/h | Brief target metric (performance). | PASS
Where the money goes — capex by category
Deterministic roll-up of every bill-of-materials line, grouped by equipment category. Sums to the bill-of-materials grand total.
Category | Cost (£) | % of capex | Share | Cell check
Pipework & valves | 339642 | 42 | █████████████████ | PASS
Filtration & membranes | 126172 | 15.6 | ██████ | PASS
Vessels, tanks & columns | 107774 | 13.3 | █████ | PASS
Controls & instrumentation | 93229 | 11.5 | █████ | PASS
Other equipment | 65693 | 8.1 | ███ | PASS
Rotating equipment | 35295 | 4.4 | ██ | PASS
Power & electrical | 30736 | 3.8 | ██ | PASS
Enclosure | 9870 | 1.2 | ▏ | PASS
Structure & skids | 420 | 0.1 | ▏ | PASS
Cabling & power runs | 54 | 0 | ▏ | PASS
Total (bill of materials) | 808885

## Renders
Renders — photoreal views of the plant | ↑ Contents
⬤ TAB QUALITY 9.7/10 · PASS (target ≥8, live from the Quality & Audit score cell) · render mechanism: parts-ledger coverage × default-size litter × typed-shape × vision-critic verdict (render-vision-critique.json) — drawing part coverage (blender) 29/30… · full audit: Quality & Audit tab
The informative views from the Blender scene build: interior hero isometric, annotated interior plan, and the building exterior. Every rendered view file (including the additional corner angles) is listed with its caption on the Drawings register tab; the full-resolution files live in the run folder.
Render 1 — Interior iso
Interior render — three-quarter hero perspective · plant envelope 22.1 × 24.4 × 4.5 m · principal equipment: TK-106 Drain Water Tank · TK-107 Drain Water Tank · TK-108 Fresh Water Tank · Z-101 Reverse Osmosis Skid · Z-102 Uf Module Bank
Render 2 — Interior plan
Interior render — plan view, looking down · plant envelope 22.1 × 24.4 × 4.5 m · principal equipment: TK-106 Drain Water Tank · TK-107 Drain Water Tank · TK-108 Fresh Water Tank · Z-101 Reverse Osmosis Skid · Z-102 Uf Module Bank
Render 5 — Exterior iso
Exterior render — three-quarter hero perspective · plant envelope 22.1 × 24.4 × 4.5 m · building shell + site apron (equipment enclosed)
Render 7 — Exterior FR iso
Exterior render — front-right corner perspective · plant envelope 22.1 × 24.4 × 4.5 m · building shell + site apron (equipment enclosed)

## Cost waterfall
Cost waterfall — BoM → installed ASP | [7 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · cost-waterfall arithmetic ties (each step vs its named costStack anchor; sums close) — waterfall rows tie live to their stated costStack anchor 6/6; assembly/install row… · full audit: Quality & Audit tab
Running build-up. Yellow = editable step £; the Running total column is LIVE (each = previous running + this step), so Σ bars = total by construction and editing any step recomputes the installed price. The assembly (B6) and installation (B9) bars are ENGINEERING ESTIMATES derived from the bill's own class subtotals × Lang/Hand-style install factors (derivation table below, sources per line) — never bare numbers. 'costStack anchor' shows the engine's stored figure at each milestone so any divergence is visible.
Step | Step £ (editable) | Running total £ (live) | Basis / derivation (costStack anchor for cross-check) | Cell check
Raw materials (BoM) | 808885 | 808885 | ​= Σ Bill of Materials (Ledger) line £ — LIVE link to the bill; edit the bill and this recomputes · engine anchor £808,885 | PASS
​+ Assembly / erection labour | 114585.11 | 923470.11 | ESTIMATE — Σ BoM class subtotals × assembly-&-integration factor: Vessels & tanks 0.10 · Piping & fittings 0.08 · Rotating machinery 0.15 · Electrical & power 0.20 · Instruments, valves & controls 0.10 · Structural & civil 0.05 · Other equipment 0.10 (LIVE from the derivation table below; Lang/Hand-style factors, sources per line). Engine assembly_labour_gbp kept as anchor · engine anchor £323,554 | PASS
​= Factory COGS |  | 923470.11 | factory_cogs_gbp (anchor — compare running total) · engine anchor £1,132,439 | PASS
​= OEM transfer price |  | 923470.11 | oem_transfer_price_gbp (anchor) · engine anchor £1,132,439 | PASS
​+ Installation / field erection | 311310.7 | 1234780.81 | ESTIMATE — Σ BoM class subtotals × install factor: Vessels & tanks 0.45 · Piping & fittings 0.60 · Rotating machinery 0.30 · Electrical & power 0.35 · Instruments, valves & controls 0.40 · Structural & civil 0.50 · Other equipment 0.30 (LIVE from the derivation table below; Lang/Hand-style factors, sources per line). Engine installation_cost_gbp kept as anchor · engine anchor £242,666 | PASS
​= Installed ASP (process equipment) |  | 1234780.81 | installed_asp_gbp (anchor — process plant installed price) · engine anchor £1,375,105 | PASS
B6 / B9 derivation — BoM class subtotals × Lang/Hand-style factors (Lang 1948 · Hand 1958 · Peters/Timmerhaus/West 5e Tbl 6-5 · Towler & Sinnott)
Equipment class | BoM subtotal £ | Lines / mass | Factor source (assembly + install) | Assembly f | Assembly £ (live) | Install f | Install £ (live) | Cell check
Vessels & tanks | 111788 | 8 line(s) · 3,448 kg | vessel/tank setting + field erection ≈ 40–50% of purchased (P,T&W 5e Tbl 6-5 install 25–55%; Hand 1958 vessel family) | 0.1 | 11178.8 | 0.45 | 50304.6 | PASS
Piping & fittings | 64182 | 52 line(s) | pipework erection is the labour-dominant field trade ≈ 50–70% of material (Towler & Sinnott piping factor; P,T&W 5e) | 0.08 | 5134.56 | 0.6 | 38509.2 | PASS
Rotating machinery | 41345 | 9 line(s) | machine setting, alignment + commissioning ≈ 25–60% of purchased, mid 30% (P,T&W 5e Tbl 6-5; Hand 1958 pump family) | 0.15 | 6201.75 | 0.3 | 12403.5 | PASS
Electrical & power | 333710 | 48 line(s) | panel wiring/integration ~20%; field electrical (containment, pulling, termination, test) ≈ 15–40% (P,T&W 5e; Towler & Sinnott f_el) | 0.2 | 66742 | 0.35 | 116798.5 | PASS
Instruments, valves & controls | 141049 | 29 line(s) | instrument mounting, hook-up, loop check + calibration ≈ 30–50% (Towler & Sinnott f_i; ISA installation norms) | 0.1 | 14104.9 | 0.4 | 56419.6 | PASS
Structural & civil | 9160 | 6 line(s) | steelwork trial-fit ~5%; site erection ≈ 50% of fabricated-steel cost (UK structural-erection norms; P,T&W civil factors) | 0.05 | 458 | 0.5 | 4580 | PASS
Other equipment | 107651 | 38 line(s) | ASSUMPTION — no class signal on these lines; generic process-equipment install 30% (P,T&W 5e 25–55% band, low end) + 10% assembly | 0.1 | 10765.1 | 0.3 | 32295.3 | PASS
Σ — feeds the ladder: B6 = ΣF, B9 = ΣH (live) | 808885 |  |  |  | 114585.11 |  | 311310.7
Reconciliation: Σ bars = the ladder's running total by construction (col C is live off col B; B6/B9 are live off this table). The engine's costStack anchors (assembly £323,554 · install £242,666 — blanket class factors) are shown per bar for cross-check; a divergence between the class-derived estimate and the blanket anchor is DISCLOSED, never hidden.

## Financial model
Financial model — cost of service first · speculative model in the appendix | [7 empty] | ↑ Contents
⬤ TAB QUALITY 8.7/10 · PASS (target ≥8, live from the Quality & Audit score cell) · formula integrity (cells reference drivers; no orphan literals) + scenario arithmetic (live) — model value cells are live formulas or declared (yellow) inputs 193/223; c… · full audit: Quality & Audit tab
THE VALID FRAME LEADS: this plant is a cost subsystem, so the tab opens with its lifecycle cost-of-service model (capex + opex + levelised £/unit), every cell live over the yellow 'Inputs & Assumptions' tab. The revenue/EBITDA/NPV/IRR machinery survives only as a clearly-labelled APPENDIX at the bottom — one caveat, stated once. Money £#,##0; margins 0.0%; years 0.0.
COST-OF-SERVICE MODEL — the lifecycle cost of the delivered service
Levelised cost of delivered treated water = (capex annualised at CRF 0.117 over 20 yr + annual opex) ÷ annual delivered volume (design flow 90 m³/h × 8760 h × water utilisation 0.25 (Inputs & Assumptions)). Every value cell is a LIVE formula over the yellow Inputs & Assumptions drivers — edit an input and this recomputes.
Item | Value (£) |  | Basis | Cell check
All-in capex | 1375105 |  | live from Inputs — installed capex (engine costStack all-in / installed ASP) | PASS
Annualised capex / yr | 161519.3173 |  | capex × CRF (live off the Inputs discount rate + project life; as-built i=10%, n=20 yr) | PASS
Energy / yr | 41340 |  | live from Inputs — connected load × hours × ELECTRICAL load factor × £/kWh (as-built 53 kW × 8,000 h × 65% × £0.15/kWh) | PASS
Maintenance / yr | 41253.15 |  | live from Inputs — 3% of capex/yr | PASS
Labour + other opex / yr | 52502 |  | live from Inputs — labour £25,000 + other opex £27,502 (the Inputs basis: unmanned/skid plant unless a headcount signal exists) | PASS
TOTAL annual opex / yr | 135095.15 |  | energy + maintenance + labour + other (sum of the live rows above)
Annual delivered volume (m³/yr) | 197100 |  | live — design flow (Inputs driver) × 8760 h × water utilisation (Inputs driver); as-built design flow 90 m³/h × 8760 h × water utilisation 0.25 (Inputs & Assumptions). The electrical load factor sizes the energy line above, never this divisor | PASS
LEVELISED COST (£/m³) | 1.5049 |  | (annualised capex + total opex) ÷ annual delivered volume — live; as-built £1.50/m³ over 197,100 m³/yr | PASS
Sweet spot & brief reconciliation
Reconciliation verdict — COMPATIBLE — the brief's cost ceiling and output target fit together
The brief is internally consistent: 360,000 m³/yr fits within the £1.40M ceiling. Recommended operating point: 360,000 m³/yr at £621k (£2/m³/yr). Objective: BALANCED (the best cost/output compromise).
Primary objective followed: BALANCED — the best cost/output compromise
Recommended operating point | Value | [6 empty] | Cell check
Recommended output (m³/yr) | 360000 | [6 empty] | PASS
Recommended capex (£) | 621316 | [6 empty] | PASS
Recommended £/m³/yr | 1.7259 | [6 empty] | PASS
Recommended scale vs brief (×) | 1 | [6 empty] | PASS
Within cost ceiling? | Yes | [6 empty] | PASS
Meets hard output floor? | Yes | [6 empty] | PASS
Cost–output frontier (capacity-scaling law) — £/unit falls with scale (economies of scale)
Output (m³/yr) | Capex (£) | £/m³/yr | [5 empty] | Cell check
90000 | 252333 | 2.8037 | [5 empty] | PASS
113392.8945 | 293222 | 2.5859 | [5 empty] | PASS
142866.0947 | 340737 | 2.385 | [5 empty] | PASS
180000 | 395953 | 2.1997 | [5 empty] | PASS
226785.789 | 460115 | 2.0289 | [5 empty] | PASS
285732.1894 | 534674 | 1.8712 | [5 empty] | PASS
360000 | 621316 | 1.7259 | [5 empty] | PASS
453571.578 | 721998 | 1.5918 | [5 empty] | PASS
571464.3787 | 838994 | 1.4681 | [5 empty] | PASS
720000 | 974949 | 1.3541 | [5 empty] | PASS
907143.1559 | 1132936 | 1.2489 | [5 empty] | PASS
1142928.7574 | 1316523 | 1.1519 | [5 empty] | PASS
1440000 | 1529860 | 1.0624 | [5 empty] | PASS
APPENDIX — if the treated water were sold (speculative — not the valid frame for this plant)
⚠ SPECULATIVE APPENDIX — no per-unit market sale price is derivable for this product class, so every revenue / EBITDA / NPV / IRR figure below is NOT a valid investor model until a real sale price is entered on the 'Inputs & Assumptions' tab. This caveat is stated ONCE and covers the whole appendix. Note the output (count) is a per-unit product spec, not annual throughput — a £/yr P&L frame does not apply.
Economics — base case (revenue / opex / EBITDA / NPV / IRR)
Annual profit & loss
Line | £ / yr (live) | Unit | Formula | Cell check
Annual revenue | 0 | £/yr | output × sale price (£/unit) | PASS
Consumables — dosing chemicals · nutrient / fertiliser stock · filter media & membranes | 0 | £/yr | output × consumable-intensity ratio × consumables price — the classes are the plant's own (from its process/media BoM + contract lines); price them on the Inputs tab | PASS
Energy cost | 41340 | £/yr | connected load (kW) × hours × load factor × £/kWh | PASS
Labour | 25000 | £/yr | from inputs | PASS
Maintenance | 41253.15 | £/yr | capex × maint% / 100 | PASS
Other opex | 27502 | £/yr | from inputs | PASS
Total opex | 135095.15 | £/yr | Σ feed + energy + labour + maintenance + other
EBITDA | -135095.15 | £/yr | revenue − total opex | PASS
Headline metrics (live)
EBITDA margin | n/a — no revenue basis |  | EBITDA ÷ revenue
Simple payback | n/a (EBITDA≤0) | yr | capex ÷ EBITDA (only if EBITDA > 0)
Discounted cashflow — NPV & IRR (live)
Year | Cashflow £ (live) | Discounted £ (live) | Note | Cell check
0 | -1375105 | -1375105 | capex outflow | PASS
1 | -135095.15 | -122813.7727 | EBITDA inflow (within project life) | PASS
2 | -135095.15 | -111648.8843 | EBITDA inflow (within project life) | PASS
3 | -135095.15 | -101498.9857 | EBITDA inflow (within project life) | PASS
4 | -135095.15 | -92271.8052 | EBITDA inflow (within project life) | PASS
5 | -135095.15 | -83883.4593 | EBITDA inflow (within project life) | PASS
6 | -135095.15 | -76257.6903 | EBITDA inflow (within project life) | PASS
7 | -135095.15 | -69325.173 | EBITDA inflow (within project life) | PASS
8 | -135095.15 | -63022.8845 | EBITDA inflow (within project life) | PASS
9 | -135095.15 | -57293.5314 | EBITDA inflow (within project life) | PASS
10 | -135095.15 | -52085.0285 | EBITDA inflow (within project life) | PASS
11 | -135095.15 | -47350.0259 | EBITDA inflow (within project life) | PASS
12 | -135095.15 | -43045.4781 | EBITDA inflow (within project life) | PASS
13 | -135095.15 | -39132.2528 | EBITDA inflow (within project life) | PASS
14 | -135095.15 | -35574.7753 | EBITDA inflow (within project life) | PASS
15 | -135095.15 | -32340.7048 | EBITDA inflow (within project life) | PASS
16 | -135095.15 | -29400.6407 | EBITDA inflow (within project life) | PASS
17 | -135095.15 | -26727.8552 | EBITDA inflow (within project life) | PASS
18 | -135095.15 | -24298.0502 | EBITDA inflow (within project life) | PASS
19 | -135095.15 | -22089.1365 | EBITDA inflow (within project life) | PASS
20 | -135095.15 | -20081.0332 | EBITDA inflow (within project life) | PASS
NPV |  | -2525246.1678 | Σ discounted cashflow (capex at yr 0 + discounted EBITDA) | PASS
IRR |  | n/a — no revenue basis | live =IRR over the year-0..N cashflow row (text n/a when the cashflow never turns positive) | PASS
Opex breakdown (feeds the pie chart)
Driver | £ / yr (live) | % of opex (live) |  | Cell check
Consumables — dosing chemicals · nutrient / fertiliser stock | 0 | 0% |  | PASS
Energy | 41340 | 30.6% |  | PASS
Labour | 25000 | 18.51% |  | PASS
Maintenance | 41253.15 | 30.54% |  | PASS
Other | 27502 | 20.36% |  | PASS
Revenue | 0
Total opex | 135095.15
EBITDA | -135095.15
Scenarios — scale sweep & price sensitivity
Output sweep (output, count) — capex via the tunable scaling exponent (default linear/modular); payback / NPV / IRR live per row
Output (count) | Capex £ (live) | Revenue £ (live) | Total opex £ (live) | EBITDA £ (live) | Payback yr | NPV £ (live) | IRR (live) | Cell check
1200 | 275021 | 0 | 69020.63 | -69020.63 | n/a | -862632.5315 | n/a | PASS
1487.2269 | 340848.8577 | 0 | 72974.4591 | -72974.4591 | n/a | -962121.565 | n/a | PASS
1843.2033 | 422433.0123 | 0 | 77874.6611 | -77874.6611 | n/a | -1085423.9018 | n/a | PASS
2284.3847 | 523544.8038 | 0 | 83947.7547 | -83947.7547 | n/a | -1238239.3626 | n/a | PASS
2831.1654 | 648858.2829 | 0 | 91474.4781 | -91474.4781 | n/a | -1427632.0809 | n/a | PASS
3508.8213 | 804166.2856 | 0 | 100802.7673 | -100802.7673 | n/a | -1662357.0684 | n/a | PASS
4348.678 | 996648.1435 | 0 | 112363.8357 | -112363.8357 | n/a | -1953264.8188 | n/a | PASS
5389.5592 | 1235201.634 | 0 | 126692.1119 | -126692.1119 | n/a | -2313803.0015 | n/a | PASS
6679.5815 | 1530854.3198 | 0 | 144449.9461 | -144449.9461 | n/a | -2760638.1404 | n/a | PASS
8278.378 | 1897273.1633 | 0 | 166458.2193 | -166458.2193 | n/a | -3314425.8201 | n/a | PASS
10259.8557 | 2351396.4787 | 0 | 193734.3001 | -193734.3001 | n/a | -4000765.7876 | n/a | PASS
12715.6116 | 2914216.8482 | 0 | 227539.0694 | -227539.0694 | n/a | -4851385.214 | n/a | PASS
15759.1668 | 3611751.5104 | 0 | 269435.2046 | -269435.2046 | n/a | -5905605.2928 | n/a | PASS
19531.2147 | 4476245.165 | 0 | 321359.4242 | -321359.4242 | n/a | -7212159.1002 | n/a | PASS
24206.124 | 5547660.3572 | 0 | 385712.0051 | -385712.0051 | n/a | -8831444.0899 | n/a | PASS
30000 | 6875525 | 0 | 465467.75 | -465467.75 | n/a | -10838314.3491 | n/a | PASS
Chart helper — payback capped at 40 yr (text 'n/a' breaks a chart series)
Output (count) | Payback yr (chart) | [6 empty] | Cell check
1200 | 40 | [6 empty] | PASS
1487.2269 | 40 | [6 empty] | PASS
1843.2033 | 40 | [6 empty] | PASS
2284.3847 | 40 | [6 empty] | PASS
2831.1654 | 40 | [6 empty] | PASS
3508.8213 | 40 | [6 empty] | PASS
4348.678 | 40 | [6 empty] | PASS
5389.5592 | 40 | [6 empty] | PASS
6679.5815 | 40 | [6 empty] | PASS
8278.378 | 40 | [6 empty] | PASS
10259.8557 | 40 | [6 empty] | PASS
12715.6116 | 40 | [6 empty] | PASS
15759.1668 | 40 | [6 empty] | PASS
19531.2147 | 40 | [6 empty] | PASS
24206.124 | 40 | [6 empty] | PASS
30000 | 40 | [6 empty] | PASS
Low / Central / High — sale price ±25%, energy ±25%, capex ±15% (at the base output)
Driver / metric | Low | Central | High |  |  |  |  | Cell check
Sale price (±25%) | 0 | 0 | 0 |  |  |  |  | PASS
Energy price (±25%) | 0.1125 | 0.15 | 0.1875 |  |  |  |  | PASS
Capex (±15%) | 1168839.25 | 1375105 | 1581370.75 |  |  |  |  | PASS
Revenue £ (live) | 0 | 0 | 0 |  |  |  |  | PASS
Total opex £ (live) | 118572.1775 | 135095.15 | 151618.1225
EBITDA £ (live) | -151618.1225 | -135095.15 | -118572.1775 |  |  |  |  | PASS
Payback yr (live) | n/a | n/a | n/a |  |  |  |  | PASS
What-if sensitivity — one driver at a time (±20%), with the EBITDA swing (tornado magnitude); held at the base output
Driver (±20%) | EBITDA @ −20% | EBITDA @ base | EBITDA @ +20% | Swing £ (¦+20 − −20¦) |  |  |  | Cell check
Sale price | -135095.15 | -135095.15 | -135095.15 | 0 |  |  |  | PASS
Consumables price (dosing chemicals · nutrient / fertiliser stock · filter media & membranes) | -135095.15 | -135095.15 | -135095.15 | 0 |  |  |  | PASS
Consumable intensity ratio | -135095.15 | -135095.15 | -135095.15 | 0 |  |  |  | PASS
Energy price | -126827.15 | -135095.15 | -143363.15 | 16536 |  |  |  | PASS
Capex (→ maintenance) | -126844.52 | -135095.15 | -143345.78 | 16501.26 |  |  |  | PASS
Labour | -130095.15 | -135095.15 | -140095.15 | 10000 |  |  |  | PASS
Breakeven & combined corners (live)
Breakeven sale price (£/unit) | 22.5159 | EBITDA = 0 at this price (vs the Inputs price)
Combined corners → EBITDA £ | Worst | Base | Best
EBITDA (all drivers swung together) | -149551.1225 | -135095.15 | -120639.1775
Low | -151618.1225
Investment analysis — the sweet-spot finder
High | -118572.1775
★ CAPEX → MAX OUTPUT — type a capex budget in the yellow cell; read the biggest plant it buys + its economics (via the tunable scaling exponent)
Capex budget (EDIT me) £ | 1375105
→ Max production (count) | 6000
→ Revenue / yr £ | 0
→ Operating cost / yr £ (interp. from sweep) | 135095.15
→ EBITDA / yr £ | -135095.15
→ Simple payback (yr) | n/a (EBITDA ≤ 0)
→ IRR (annuity) | n/a
DEPLOYMENT VERDICT
NO DEPLOYMENT RECOMMENDED — EBITDA is negative at every scale in the 0.2x–5x sweep at the current inputs (no revenue basis), so there is no point worth deploying capital into. The valid economics for this plant are the cost-of-service model at the top of this tab.
Sweet-spot thresholds — live over the scale sweep (Scenarios tab)
What | Output (count) | Capex £ | IRR | Payback yr | How it's found | Cell check
Break-even scale (EBITDA ≥ 0) | none in range (all EBITDA < 0) | — | — | — | first sweep row with EBITDA ≥ 0 (EBITDA rises with scale); 'none in range' when every sweep row is loss-making
Viability threshold (IRR ≥ discount rate) | > range | — | — | — | first row whose IRR clears the discount rate — capital just covers its cost | ⚠ FAIL — a required cell is empty/placeholder or wrong type
Investable scale (IRR ≥ hurdle) | > range | — | — | — | first row whose IRR clears the editable investor hurdle (Inputs tab) — the SWEET SPOT | ⚠ FAIL — a required cell is empty/placeholder or wrong type
NPV-max scale (in range) | 1200 | 275021 | n/a | n/a | output that maximises NPV across the sweep (trends to the top of the range when economics improve with scale) | PASS
What moves the sweet spot
The SALE PRICE per output unit is the dominant lever (revenue is linear in it and in output). ENERGY price + connected load set the largest variable-opex line. CAPEX and its six-tenths exponent set the absolute investment and the maintenance line. Flex these on the Inputs tab — every threshold + curve moves live.
[7 empty] | Capex £ | Output count | IRR | Discount-rate line | Hurdle line | NPV £ | Payback yr (cap 40) | EBITDA margin
[7 empty] | 275021 | 1200 | 0% | 10% | 15% | -862632.5315 | 40 | 0%
[7 empty] | 340848.8577 | 1487.2269 | 0% | 10% | 15% | -962121.565 | 40 | 0%
[7 empty] | 422433.0123 | 1843.2033 | 0% | 10% | 15% | -1085423.9018 | 40 | 0%
[7 empty] | 523544.8038 | 2284.3847 | 0% | 10% | 15% | -1238239.3626 | 40 | 0%
[7 empty] | 648858.2829 | 2831.1654 | 0% | 10% | 15% | -1427632.0809 | 40 | 0%
[7 empty] | 804166.2856 | 3508.8213 | 0% | 10% | 15% | -1662357.0684 | 40 | 0%
[7 empty] | 996648.1435 | 4348.678 | 0% | 10% | 15% | -1953264.8188 | 40 | 0%
[7 empty] | 1235201.634 | 5389.5592 | 0% | 10% | 15% | -2313803.0015 | 40 | 0%
[7 empty] | 1530854.3198 | 6679.5815 | 0% | 10% | 15% | -2760638.1404 | 40 | 0%
[7 empty] | 1897273.1633 | 8278.378 | 0% | 10% | 15% | -3314425.8201 | 40 | 0%
[7 empty] | 2351396.4787 | 10259.8557 | 0% | 10% | 15% | -4000765.7876 | 40 | 0%
[7 empty] | 2914216.8482 | 12715.6116 | 0% | 10% | 15% | -4851385.214 | 40 | 0%
[7 empty] | 3611751.5104 | 15759.1668 | 0% | 10% | 15% | -5905605.2928 | 40 | 0%
[7 empty] | 4476245.165 | 19531.2147 | 0% | 10% | 15% | -7212159.1002 | 40 | 0%
[7 empty] | 5547660.3572 | 24206.124 | 0% | 10% | 15% | -8831444.0899 | 40 | 0%
[7 empty] | 6875525 | 30000 | 0% | 10% | 15% | -10838314.3491 | 40 | 0%

## Bill of Materials (Ledger)
Bill of Materials (Ledger) | [14 empty] | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · column-contract arithmetic: 10 × 435/435 rows passing; content checks: BoM ledger column contract (per-row Row check) — cell completeness+type contract 3038/3061 · score… · full audit: Quality & Audit tab
THE BILL + its provenance + its engineering, on one sheet — ALL COLUMNS VISIBLE (nothing hidden/collapsed). Buy-list: tag · item · qty · unit £ · LIVE line £. 'Cost basis' (cols F–J) = HOW each £ was derived (method / inputs / factors / estimate class / confidence); 'Engineering spec' (cols K–N) = WHY each principal is this size (duty / material / sizing calc / MPN). Σ line £ is live at the foot; commodity lines leave the spec columns blank (correct — they need no sizing basis). ↳ SUB-COMPONENT ROWS are grouped under their parent principal and open COLLAPSED — the sheet reads as the buy list; expand a parent's + on the left margin to see its children (their £ is apportioned into the parent line). MPN STATUS: engineered TBD 32/70 bought-out lines await detailed design (score penalised by the engineered-TBD fraction — a fully-TBD bill cannot reach 8) · commodity 17/22 small parts carry 'commodity — MPN at procurement' (commodity noun family + unit £ ≤ £100, both required — unpenalised, tallied separately; real practice carries no MPN on class-basis commodity parts at concept stage). ROW CHECK CONTRACT (score = 10 × rows-passing ÷ rows − 4 × engineered-TBD-fraction = 10 × 435/435 − 4 × 0.457 = 8.2): MPN TALLIES: engineered TBD 32/70 (penalised) · commodity 'MPN at procurement' 17/22 (unpenalised, visible; commodity = noun family + unit £ ≤ £100, both required). Tag/Item=required_nonempty · Class fit=computed · Qty=required_nonempty · Unit £ / Line £=computed · Basis=required_nonempty · Material=computed · MPN / datasheet=computed. A dash / empty / unverifiable contracted cell FAILS its row — honest red beats fake green.
Tag | Item | Qty | Unit £ | Line £ | Cost method | Key inputs | Factors | Est class | Confidence | Duty / rating | Material | Sizing calc (basis) | MPN / datasheet | Row check | Audit: check evidence (build-computed) | Cell check
X-105 | Electrical Control Panel | 1 | 672 | 672 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Electrical Control Panel | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Rittal 1180.000 | PASS |  | PASS
X-106 / X-110 | Circuit Breaker | 2 | 283 | 566 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Circuit Breakers | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | ABB 1SDA067417R1 | PASS |  | PASS
X-107 | Motor Starter | 1 | 183 | 183 | class_reference | median £183, n=5 | 14%; £25→£183; lifted; corpus; parametric | 4 | low | Motor Starter | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · lifted £25→£183 to the engine corpus 0.6×median (median £183, n=5; line was 14% of median — under-priced vs the engine's own forge-truth reference) | TBD (detailed design) | PASS |  | PASS
X-108 / X-111 | Terminal Block | 2 | 2 | 4 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Terminal Blocks | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · commodity-floor (estimate £0.11 renders £0; 'terminal' → £2) | commodity — MPN at procurement | PASS |  | PASS
D-101 | 3 Phase Power Input | 1 | 148 | 148 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | 3 Phase Power Input | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | TDK-Lambda DRB240-24-3-A0 | PASS |  | PASS
X-109 | DC Power Cabling | 1 | 3 | 3 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | DC Power Cabling | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
G-201 | Standby Diesel Generator · 60 kVA · 862x733x948 mm | 1 | 19200 | 19200 | class_reference | 60 kVA | £320/kVA; install; rating-based | 4 | low | Standby Diesel Generator · 60 kVA · 862x733x948 mm | N/A — proprietary assembly / bought-out package, see datasheet | rating-based: 60 kVA × £320/kVA (UK-2026 installed mid; band £200-440/kVA) — standby diesel genset @ £/kVA [£44,840 above band → grounded to market] | Pramac GBW60P | PASS |  | PASS
U-201 | Control + Instrument UPS · 5 kW (30 min) · 600x510x660 mm | 1 | 4000 | 4000 | class_reference | 5 kVA | £550/kVA; install; rating-based | 4 | moderate | Control + Instrument UPS · 5 kW (30 min) · 600x510x660 mm | N/A — proprietary assembly / bought-out package, see datasheet | rating-based: 5 kVA × £550/kVA (UK-2026 installed mid; band £300-950/kVA) — UPS @ £/kVA [£21,500 above band → grounded to market] | Eaton 9SX5KI | PASS |  | PASS
EP-103 | SCADA / Plant Control System · 53 kW plant | 1 | 62650 | 62650 | class_reference | 53 kW | £50/kW; install; class budget; catalogue | 4 | low | SCADA / Plant Control System · 53 kW plant | N/A — proprietary assembly / bought-out package, see datasheet | installed process system — catalogue-class budget: £60k base (redundant PLC racks + SCADA servers + operator HMIs + I/O + plant network + software licences + panel build + commissioning; supply + install) + £50/kW × ~53 kW connected plant load | Hoogendoorn iSii | PASS |  | PASS
EP-104 | Motor Control Center | 1 | 3000 | 3000 | llm_estimate | model estimate (no itemised inputs) | floored; parametric | 5 | low | Motor Control Center | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · floored to min credible price | TBD (detailed design) | PASS |  | PASS
INV-1 | Vfd Drive | 1 | 1086 | 1086 | class_reference | median £1,927, n=5 | 11%; £218→£1,086; lifted; corpus; parametric | 4 | low | Vfd Drive | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · lifted £218→£1,086 to the engine corpus p25 (median £1,927, n=5; line was 11% of median — under-priced vs the engine's own forge-truth reference) | TBD (detailed design) | PASS |  | PASS
INV-2 | Vfd Controller | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Vfd Controller | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
F-1 | Ro Membrane Elements · 364 m² area | 1 | 9100 | 9100 | llm_estimate | 364 m² | £25/m²; take-off; parametric | 5 | low | Ro Membrane Elements · 364 m² area | membrane/filtration media | membrane-area parametric: 364 m² × £25/m² (spiral-wound/UF module supply, UK-2026; NOT a steel take-off) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
—.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103 | Ultrafiltration Module | 1 | 14825 | 0 | llm_estimate |  | parametric | 5 | low |  |  |  |  | FAIL — line ≠ qty×unit, a required cell empty, or qty/£ non-positive |  | PASS
Z-103.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-103.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-103.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-102 | Piping Network | 1 | 9 | 9 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Piping Network | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
X-112 / V-111 | Check Valve | 2 | 9 | 18 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Check Valves | PVC-U / 304 stainless (WRAS) | bottom-up parametric · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | commodity — MPN at procurement | PASS |  | PASS
X-113 | Hydraulic Connectors | 1 | 1 | 1 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Hydraulic Connectors | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
V-102 | Uv Disinfection · 4 kW · 600x510x660 mm | 1 | 17540 | 17540 | class_reference | median £34,360, n=5 | 35%; £12,012→£17,540; lifted; corpus; catalogue | 4 | low | Uv Disinfection · 4 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) · lifted £12,012→£17,540 to the engine corpus p25 (median £34,360, n=5; line was 35% of median — under-priced vs the engine's own forge-truth reference) | WEDECO (Xylem) Spektron 30e | PASS |  | PASS
V-102.1 | ↳ Process Unit | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-102.2 | ↳ Inlet / Outlet Manifolds | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-102.3 | ↳ Flow Control Valve | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-102.4 | ↳ Dosing / Lamp Module | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-102.5 | ↳ Local Sensor | 1 | incl. in parent | — | class_reference |  | catalogue | 4 | low |  |  |  |  | PASS |  | PASS
V-102.6 | ↳ Control & Power Module | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-102.7 | ↳ Mounting Frame | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106 | Softener Vessel · 1.2 m dia x 1.3 m | 2 | 8000 | 16000 | class_reference | 5 mm; 1.3 m; 13 kPa; 120 MPa; 6 m²; 259 kg; median £12,581 | ×1.3; × 259; £4.5/kg; × 1.25; 28%; £3,548→£8,000; lifted; | 4 | low | Softener Vessel · 1.2 m dia x 1.3 m | carbon steel | tapered wall 5 mm = P·r/(σ·E)+c · ⌀1.2×1.3 m (open top (no head)) · P=13 kPa head · σ=120 MPa → 6 m² × 259 kg carbon steel @ £4.5/kg supply × 1.25 erection + fittings · named part Pentair Structural '36X72 COMP 6"TF 6"BF' rejected: Engine B priced it £840 via its small-parts commodity curve — no catalogue class exists for a bespoke fabricated tank/vessel shell; a materials take-off is used instead · lifted £3,548→£8,000 to the engine corpus p25 (median £12,581, n=5; line was 28% of median — under-priced vs the engine's own forge-truth reference) | Pentair Structural 36X72 COMP 6"TF 6"BF | PASS |  | PASS
V-106.1 | ↳ Shell Course | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.2 | ↳ Top Head / Roof | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.3 | ↳ Base / Floor Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.4 | ↳ Support Skirt / Legs | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-106.5 | ↳ Manway & Cover | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.6 | ↳ Inlet Nozzle Set | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.7 | ↳ Outlet Nozzle Set | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.8 | ↳ Drain Nozzle | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.9 | ↳ Overflow / Weir | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-106.10 | ↳ Internal Distribution | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.11 | ↳ Tank Vent / Pressure Relief | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-106.12 | ↳ Access Ladder & Platform | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.13 | ↳ Internal Lining / Coating | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.14 | ↳ Earthing Boss | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-106.15 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106 | Fertigation Dosing Pump · 8 kW · 600x510x660 mm | 2 | 8634 | 17268 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Fertigation Dosing Pump · 8 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Grundfos 96122012 | PASS |  | PASS
P-106.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.3 | ↳ Drive Motor · 7.5 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.4 | ↳ Variable-Speed Drive · 7.5 kW | 1 | incl. in parent | — | catalogue |  | catalogue; parametric | 2 | high |  |  |  |  | PASS |  | PASS
P-106.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-106.9 | ↳ Suction Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.10 | ↳ Discharge Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.11 | ↳ Non-Return Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-106.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103 | Nutrient Tank · 1.1 m dia x 1.1 m | 8 | 2844 | 22752 | class_reference | 6 mm; 1.1 m; 11 kPa; 18 MPa; 5 m²; 58 kg | ×1.1; × 58; £12.0/kg; × 1.25 | 4 | low | Nutrient Tank · 1.1 m dia x 1.1 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀1.1×1.1 m (open top (no head)) · P=11 kPa head · σ=18 MPa → 5 m² × 58 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-103.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-103.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.10 | ↳ Earthing Boss | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-103.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102 | Hand Watering Pump · 25 m³/h · 900x500x700 mm | 1 | 2500 | 2500 | class_reference | 3 kW | £700/kW; install; rating-based | 4 | low | Hand Watering Pump · 25 m³/h · 900x500x700 mm | PVC-U / 304 stainless (WRAS) | rating-based: 3 kW × £700/kW (UK-2026 installed mid; band £350-1300/kW) — process pump (skid: casing+motor+VSD) @ £/kW [£7,796 above band → grounded to market] · motor kW from contract hand_watering_pump_motor_kw (the line's own rating is a flow, not a power) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Grundfos 96935501 | PASS |  | PASS
P-102.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.3 | ↳ Drive Motor · 3 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.4 | ↳ Variable-Speed Drive · 3 kW | 1 | incl. in parent | — | catalogue |  | catalogue; parametric | 2 | high |  |  |  |  | PASS |  | PASS
P-102.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-102.9 | ↳ Suction Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.10 | ↳ Discharge Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.11 | ↳ Non-Return Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-102.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114 | Drain Collection Sump · 2.1 m dia x 1.4 m | 2 | 4683 | 9366 | class_reference | 6 mm; 1.4 m; 14 kPa; 18 MPa; 13 m²; 160 kg | ×1.4; × 160; £12.0/kg; × 1.25 | 4 | low | Drain Collection Sump · 2.1 m dia x 1.4 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀2.1×1.4 m (open top (no head)) · P=14 kPa head · σ=18 MPa → 13 m² × 160 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-114.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-114.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.10 | ↳ Earthing Boss | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-114.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104 | Drain Transfer Pump · 2 kW · 600x510x660 mm | 2 | 1850 | 3700 | class_reference | 2kw |  | 4 | low | Drain Transfer Pump · 2 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | real DB median of 1 comparable 2kw 'pump' parts (forge-truth.db) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | TBD (detailed design) | PASS |  | PASS
P-104.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.3 | ↳ Drive Motor · 2.2 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.4 | ↳ Variable-Speed Drive · 2.2 kW | 1 | incl. in parent | — | catalogue |  | catalogue; parametric | 2 | high |  |  |  |  | PASS |  | PASS
P-104.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-104.9 | ↳ Suction Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.10 | ↳ Discharge Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.11 | ↳ Non-Return Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-104.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-103 | Cloth Filter · 80 m³/h · 3 m² area | 2 | 8270 | 16540 | llm_estimate | 3 m²; 0 bar | £90/m²; take-off | 5 | low | Cloth Filter · 80 m³/h · 3 m² area | structural steel | structural steelwork take-off: 3 m² plan × £90/m² (UK-2026 fabricated + erected; service=structural, dry, 0 bar — NOT a pressure shell) + £8k connections | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
V-103.1 | ↳ Drum / Element · 80 m³/h | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-103.2 | ↳ Media / Mesh Panels | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.3 | ↳ Drive Gearmotor · 1 kW | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-103.4 | ↳ Backwash Spray Bar | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.5 | ↳ Backwash Pump | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.6 | ↳ Reject Trough | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-103.7 | ↳ Differential-Pressure Switch | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | moderate |  |  |  |  | PASS |  | PASS
V-103.8 | ↳ Support Frame | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-103.9 | ↳ Local Control Panel | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-105 | Gac Softener · 15 m³/h · 0.9 m dia x 1.8 m | 1 | 14825 | 14825 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Gac Softener · 15 m³/h · 0.9 m dia x 1.8 m | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
V-105.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-105.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-105.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-105.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-105.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-105.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-105.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-105.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-105.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-105.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103 | Irrigation Pump · 90 m³/h · 1379x766x1073 mm | 1 | 9413 | 9413 | class_reference | 45 m³ | × 2; catalogue | 4 | low | Irrigation Pump · 90 m³/h · 1379x766x1073 mm | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | Grundfos 96539165 | PASS |  | PASS
P-103.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.3 | ↳ Drive Motor · 11 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.4 | ↳ Variable-Speed Drive · 11 kW | 1 | incl. in parent | — | catalogue | incl. in parent line |  | 2 | high |  |  |  |  | PASS |  | PASS
P-103.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-103.9 | ↳ Suction Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.10 | ↳ Discharge Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.11 | ↳ Non-Return Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-103.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
M-101 | Distribution Manifold · 45 m³/h · 700x595x770 mm | 2 | 1725 | 3450 | class_reference | 45 m³ | parametric | 4 | low | Distribution Manifold · 45 m³/h · 700x595x770 mm | PVC-U / 304 stainless (WRAS) | distribution-manifold parametric: 45 m³/h delivery duty × £25/(m³·h) + £600 base — fabricated header + isolation/non-return valves + gauge tappings + supports (supply-only materials; field labour in the cost stack) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
Z-101 | Reverse Osmosis Skid · 2.3 m dia x 2.4 m | 1 | 8737 | 8737 | class_reference | 8 m²; 0 bar | £90/m²; take-off | 4 | low | Reverse Osmosis Skid · 2.3 m dia x 2.4 m | structural steel | structural steelwork take-off: 8 m² plan × £90/m² (UK-2026 fabricated + erected; service=structural, dry, 0 bar — NOT a pressure shell) + £8k connections | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
Z-101.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-101.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-101.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101 | Ro High Pressure Pump · 4 kW · 600x510x660 mm | 1 | 3850 | 3850 | class_reference | 4kw |  | 4 | low | Ro High Pressure Pump · 4 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | real DB median of 1 comparable 4kw 'pump' parts (forge-truth.db) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | TBD (detailed design) | PASS |  | PASS
P-101.1 | ↳ Casing | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.2 | ↳ Impeller / Rotor | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.3 | ↳ Drive Motor · 4.2 kW | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.4 | ↳ Variable-Speed Drive · 4.2 kW | 1 | incl. in parent | — | catalogue | incl. in parent line |  | 2 | high |  |  |  |  | PASS |  | PASS
P-101.5 | ↳ Flexible Coupling | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.6 | ↳ Coupling Guard | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.7 | ↳ Baseplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.8 | ↳ Mechanical Seal | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
P-101.9 | ↳ Suction Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.10 | ↳ Discharge Isolation Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.11 | ↳ Non-Return Valve | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.12 | ↳ Discharge Pressure Gauge | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
P-101.13 | ↳ Anti-Vibration Mounts | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101 | Gac Filter · 1.3 m dia x 1.4 m | 1 | 14825 | 14825 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Gac Filter · 1.3 m dia x 1.4 m | PVC-U / 304 stainless (WRAS) | bottom-up parametric · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | TBD (detailed design) | PASS |  | PASS
V-101.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-101.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
V-101.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108 | Fresh Water Tank · 3.7 m dia x 3.7 m | 1 | 13615 | 13615 | class_reference | 6 mm; 3.7 m; 36 kPa; 18 MPa; 54 m²; 656 kg | ×3.7; × 656; £12.0/kg; × 1.25 | 4 | low | Fresh Water Tank · 3.7 m dia x 3.7 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀3.7×3.7 m (open top (no head)) · P=36 kPa head · σ=18 MPa → 54 m² × 656 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-108.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-108.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.10 | ↳ Earthing Boss | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-108.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106 | Drain Water Tank · 3.7 m dia x 3.7 m | 2 | 13615 | 27230 | class_reference | 6 mm; 3.7 m; 36 kPa; 18 MPa; 54 m²; 656 kg | ×3.7; × 656; £12.0/kg; × 1.25 | 4 | low | Drain Water Tank · 3.7 m dia x 3.7 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀3.7×3.7 m (open top (no head)) · P=36 kPa head · σ=18 MPa → 54 m² × 656 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-106.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-106.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.10 | ↳ Earthing Boss | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-106.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-114 | Compartment Spacers | 1 | 3 | 3 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | moderate | Compartment Spacers | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · commodity-floor (estimate £0.11 renders £0; 'spacers' → £3) | commodity — MPN at procurement | PASS |  | PASS
F-2 | Uf Membrane Bank · 364 m² area | 1 | 9100 | 9100 | class_reference | 364 m² | £25/m²; take-off; parametric | 4 | low | Uf Membrane Bank · 364 m² area | membrane/filtration media | membrane-area parametric: 364 m² × £25/m² (spiral-wound/UF module supply, UK-2026; NOT a steel take-off) · merged synonym line(s): 'Ultrafiltration Module' (was £14,825), 'Uf Module Bank' (was £14,825) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
—.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102 | Uf Module Bank | 1 | 14825 | 0 | class_reference |  | take-off | 4 | moderate |  |  |  |  | FAIL — line ≠ qty×unit, a required cell empty, or qty/£ non-positive |  | PASS
Z-102.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
Z-102.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
Z-102.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-115 / X-122 | PLC Controller | 2 | 313 | 626 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | PLC Controller | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Siemens 6ES7212-1AE40-0XB0 | PASS |  | PASS
X-116 | Veolia Ro40 Controller | 1 | 12 | 12 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Veolia Ro40 Controller | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
X-117 | Modbus Interface | 1 | 160 | 160 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Modbus Interface | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Siemens 6ES7241-1CH32-0XB0 | PASS |  | PASS
X-118 | Ethernet Ip Module | 1 | 132 | 132 | class_reference | median £324, n=5 | 4%; £12→£132; lifted; corpus; parametric | 4 | low | Ethernet Ip Module | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · lifted £12→£132 to the engine corpus p25 (median £324, n=5; line was 4% of median — under-priced vs the engine's own forge-truth reference) | TBD (detailed design) | PASS |  | PASS
X-119 | Hoogendoorn iSii Remote Monitoring | 1 | 985 | 985 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Hoogendoorn iSii Remote Monitoring | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | HMS Networks (Ewon) FLEXY20500_00MA | PASS |  | PASS
X-120 | Dc3 Power Controller | 1 | 12 | 12 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Dc3 Power Controller | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
X-121 | HMI Touchscreen | 1 | 595 | 595 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | HMI Touchscreen | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Panasonic Industrial Automation AWHS1R070 | PASS |  | PASS
X-123 | Modbus Tcp Interface | 1 | 3 | 3 | llm_estimate | model estimate (no itemised inputs) | catalogue | 5 | low | Modbus Tcp Interface | N/A — proprietary assembly / bought-out package, see datasheet | catalogue · commodity-floor (no DB price; 'interface' → £3) | HMS Networks AB7072-B | PASS |  | PASS
X-124 | Remote Monitoring Gateway | 1 | 500 | 500 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 4 | moderate | Remote Monitoring Gateway | N/A — proprietary assembly / bought-out package, see datasheet | catalogue · commodity ceiling · capped at £500 for a bare remote monitoring gateway (was £985; no kW/duty rating — a catalogue part, not a bespoke instrument) | HMS Networks (Ewon) FLEXY20500_00MA | PASS |  | PASS
I-103 | Digital Control Panel | 1 | 800 | 800 | class_reference | class-reference price (no itemised inputs) | floored; parametric | 4 | low | Digital Control Panel | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · floored to min credible price | TBD (detailed design) | PASS |  | PASS
X-125 / V-107 | Solenoid Valve | 2 | 424 | 848 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Solenoid Valves | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Sensata Technologies, Inc. SOL7A4 | PASS |  | PASS
X-126 | Pneumatic Actuated Valves | 200 | 200 | 40000 | class_reference | class-reference price (no itemised inputs) | £1.85/DN·mm | 4 | low | Pneumatic Actuated Valves | PVC-U / 304 stainless (WRAS) | actuated-valve assembly (actuator + valve body as ONE unit): £80 base + £1.85/DN·mm × DN65 assumed (2½ in class) = £200 (UK-2026 trade supply, never the bare-valve band) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Bürkert Type 2000 | PASS |  | PASS
X-127 | Manual Isolation Valves | 1 | 95 | 95 | llm_estimate | model estimate (no itemised inputs) | floored; parametric | 5 | low | Manual Isolation Valves | PVC-U / 304 stainless (WRAS) | bottom-up parametric · floored to min credible price · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | commodity — MPN at procurement | PASS |  | PASS
— | Pneumatic Actuators | 200 | 30 | 0 | class_reference |  | floored; parametric | 4 | low |  |  |  |  | FAIL — line ≠ qty×unit, a required cell empty, or qty/£ non-positive |  | ⚠ FAIL — 'Tag' placeholder '—'
X-128 | Flow Control Valves | 1 | 18 | 18 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Flow Control Valves | PVC-U / 304 stainless (WRAS) | catalogue · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Pentair Fleck 2900S | PASS |  | PASS
FCV-201–202 | Inlet Flow Control Valve · 45 m³/h · DN100 modulating control valve (45 m³/h @ 2 m/s) | 2 | 3312 | 6624 | class_reference | class-reference price (no itemised inputs) | install; class budget; catalogue | 4 | low | Inlet Flow Control Valve · 45 m³/h · DN100 modulating control valve (45 m³/h @ 2 m/s) | N/A — proprietary assembly / bought-out package, see datasheet | installed actuator — catalogue-class budget | TBD (detailed design) | PASS |  | PASS
V-108 / X-129 | Manual Ball Valve | 2 | 9 | 18 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Manual Ball Valve | PVC-U / 304 stainless (WRAS) | bottom-up parametric · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | commodity — MPN at procurement | PASS |  | PASS
V-109 | Pneumatic Control Valve | 1 | 200 | 200 | class_reference | class-reference price (no itemised inputs) | £1.85/DN·mm | 4 | low | Pneumatic Control Valve | PVC-U / 304 stainless (WRAS) | actuated-valve assembly (actuator + valve body as ONE unit): £80 base + £1.85/DN·mm × DN65 assumed (2½ in class) = £200 (UK-2026 trade supply, never the bare-valve band) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Bürkert Type 2301 | PASS |  | PASS
X-130 | Automated Ball Valves | 1 | 200 | 200 | class_reference | class-reference price (no itemised inputs) | £1.85/DN·mm | 4 | low | Automated Ball Valves | PVC-U / 304 stainless (WRAS) | actuated-valve assembly (actuator + valve body as ONE unit): £80 base + £1.85/DN·mm × DN65 assumed (2½ in class) = £200 (UK-2026 trade supply, never the bare-valve band) · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | TBD (detailed design) | PASS |  | PASS
I-104 | Conductivity Sensor | 1 | 80 | 80 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Conductivity Sensor | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
I-105 / X-131 | Flow Meter | 2 | 152 | 304 | catalogue | catalogue-class budget (no itemised inputs) | parametric | 2 | high | Flow Meter | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | Sensirion SFM4100-Air, N2 Downmount | PASS |  | PASS
I-106 | Ph Sensor | 1 | 80 | 80 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Ph Sensor | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
I-107 | Orp Sensor | 1 | 80 | 80 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | moderate | Orp Sensor | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
LT-201–213 | Level Transmitter · 0–1.4 m | 13 | 900 | 11700 | llm_estimate | 1.4 m | ×2; ×8; ×1; install; class budget; catalogue | 5 | low | Level Transmitter · 0–1.4 m | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget · qty 13 = one per monitored vessel (a contract-declared control variable is measured on EVERY vessel that holds it — stated engineering rule); locations: softener vessel ×2 (0–1.4 m), nutrient tank ×8 (0–1.4 m), drain collection sump ×2 (0–1.4 m), gac filter ×1 (0–1.4 m) | Endress+Hauser Waterpilot FMX21 | PASS |  | PASS
LT-214 | Level Transmitter · 0–3 m | 1 | 900 | 900 | llm_estimate | model estimate (no itemised inputs) | install; class budget; catalogue | 5 | low | Level Transmitter · 0–3 m | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget | Endress+Hauser Waterpilot FMX21 | PASS |  | PASS
LT-215–217 | Level Transmitter · 0–4 m | 3 | 900 | 2700 | llm_estimate | 4 m | ×1; ×2; install; class budget; catalogue | 5 | low | Level Transmitter · 0–4 m | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget · qty 3 = one per monitored vessel (a contract-declared control variable is measured on EVERY vessel that holds it — stated engineering rule); locations: fresh water tank ×1 (0–4 m), drain water tank ×2 (0–4 m) | Endress+Hauser Waterpilot FMX21 | PASS |  | PASS
AT-201 | pH Analyser · pH 0–14 (control 0.3) | 1 | 1300 | 1300 | llm_estimate | model estimate (no itemised inputs) | install; class budget; catalogue | 5 | low | pH Analyser · pH 0–14 (control 0.3) | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget | Hach LXV404.99.05112 | PASS |  | PASS
PT-201–217 | Pressure Transmitter · 0–5 bar | 17 | 700 | 11900 | catalogue | 5 bar | ×2; ×8; ×1; install; class budget; catalogue | 2 | high | Pressure Transmitter · 0–5 bar | N/A — proprietary assembly / bought-out package, see datasheet | installed instrument — catalogue-class budget · qty 17 = one per monitored vessel (a contract-declared control variable is measured on EVERY vessel that holds it — stated engineering rule); locations: softener vessel ×2 (0–5 bar), nutrient tank ×8 (0–5 bar), drain collection sump ×2 (0–5 bar), reverse osmosis skid ×1 (0–5 bar), gac filter ×1 (0–5 bar), fresh water tank ×1 (0–5 b | Telemecanique XMLP150PD130 | PASS |  | PASS
I-108 | Silica Analyzer | 1 | 280 | 280 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Silica Analyzer | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Hach 5500sc | PASS |  | PASS
I-109 | Chlorine Sensor | 1 | 80 | 80 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Chlorine Sensor | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
I-110 | Tds Sensor | 1 | 30 | 30 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Tds Sensor | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
EP-102 | Mains Incomer · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | 1 | 3 | 3 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Mains Incomer · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
EP-101 | Main Switchboard · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | 1 | 3000 | 3000 | class_reference | class-reference price (no itemised inputs) | floored; parametric | 4 | moderate | Main Switchboard · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · floored to min credible price | TBD (detailed design) | PASS |  | PASS
X-132 | Power Supply Unit | 1 | 218 | 218 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | moderate | Power Supply Unit | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
X-133 | Surge Protection Device | 1 | 250 | 250 | catalogue | catalogue-class budget (no itemised inputs) | catalogue | 2 | high | Surge Protection Device | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Phoenix Contact 2838199 | PASS |  | PASS
X-104 | Permeate Outlet | 1 | 9 | 9 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Permeate Outlet | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
X-103 | Concentrate Outlet | 1 | 9 | 9 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Concentrate Outlet | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
X-134 | Sample Valves | 1 | 9 | 9 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Sample Valves | PVC-U / 304 stainless (WRAS) | bottom-up parametric · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | commodity — MPN at procurement | PASS |  | PASS
X-135 | Painted Steel Skid Frame · 2.3 m dia x 2.4 m | 1 | 40 | 40 | class_reference | class-reference price (no itemised inputs) |  | 4 | low | Painted Steel Skid Frame · 2.3 m dia x 2.4 m | painted structural carbon steel (S275/S355) | made-to-spec · structural budget estimate | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
X-136 | Sst304 Skid Frame · 2.3 m dia x 2.4 m | 1 | 40 | 40 | class_reference | class-reference price (no itemised inputs) |  | 4 | low | Sst304 Skid Frame · 2.3 m dia x 2.4 m | 304 stainless steel | made-to-spec · structural budget estimate | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
X-137 | Leveling Feet | 1 | 3 | 3 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Leveling Feet | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · commodity-floor (estimate £0.11 renders £0; 'feet' → £3) | commodity — MPN at procurement | PASS |  | PASS
TX-101 | Transformer · 75 kW · 1090x927x1199 mm | 1 | 3000 | 3000 | llm_estimate | 75 kVA | £28/kVA; install; rating-based | 5 | low | Transformer · 75 kW · 1090x927x1199 mm | N/A — proprietary assembly / bought-out package, see datasheet | rating-based: 75 kVA × £28/kVA (UK-2026 installed mid; band £15-55/kVA) — transformer @ £/kVA [£15 below band → grounded to market] | TBD (detailed design) | PASS |  | PASS
X-138 | Module Support System | 1 | 300 | 300 | class_reference | median £1,500, n=5 | 3%; £40→£300; lifted; corpus; parametric | 4 | low | Module Support System | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · lifted £40→£300 to the engine corpus p25 (median £1,500, n=5; line was 3% of median — under-priced vs the engine's own forge-truth reference) | TBD (detailed design) | PASS |  | PASS
X-139 | Flexmount Connectors | 1 | 1 | 1 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Flexmount Connectors | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
X-140 | Painted Carbon Steel Skid Frame · 2.3 m dia x 2.4 m | 1 | 40 | 40 | class_reference | class-reference price (no itemised inputs) |  | 4 | low | Painted Carbon Steel Skid Frame · 2.3 m dia x 2.4 m | painted structural carbon steel (S275/S355) | made-to-spec · structural budget estimate | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
F-3 | Grp Membrane Housings · 364 m² area | 1 | 11000 | 11000 | llm_estimate | 364 m²; 37 m² | × 8; take-off; parametric | 5 | low | Grp Membrane Housings · 364 m² area | membrane/filtration media | membrane-housing parametric: 364 m² membrane area ÷ 37 m²/element → 10 × 8-in GRP pressure housing @ £1,100 (UK-2026 supply; NOT a steel take-off) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
—.1 | ↳ Pressure Vessel Shell · 15 m³/h | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.2 | ↳ Filter Media / Membrane Elements | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.3 | ↳ Upper Distribution Header | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.4 | ↳ Lower Underdrain / Nozzle Plate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.5 | ↳ Backwash / Service Valve Nest | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.6 | ↳ Differential-Pressure Gauges | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.7 | ↳ Air Scour / Vent | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
—.8 | ↳ Sample Cock | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.9 | ↳ Skid Frame & Pipework | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
—.10 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
V-110 | Pressure Relief Valve · 4 kW · 600x510x660 mm | 1 | 18 | 18 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Pressure Relief Valve · 4 kW · 600x510x660 mm | PVC-U / 304 stainless (WRAS) | bottom-up parametric · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | Goetze Series 851 | PASS |  | PASS
I-111 | Low Pressure Switch | 1 | 76 | 76 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | moderate | Low Pressure Switch | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Danfoss 060-121966 | PASS |  | PASS
I-112 | High Pressure Switch | 1 | 30 | 30 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | High Pressure Switch | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
X-141 / X-144 / I-114 | Emergency Stop | 3 | 40 | 120 | class_reference | class-reference price (no itemised inputs) | floored; catalogue | 4 | moderate | Emergency Stop Button | N/A — proprietary assembly / bought-out package, see datasheet | catalogue · floored to min credible price | Eaton 216516 | PASS |  | PASS
I-102 | Electrical Control Cabinet | 1 | 8023 | 8023 | class_reference | 0 m²; 0 bar | £90/m²; take-off | 4 | low | Electrical Control Cabinet | structural steel | structural steelwork take-off: 0 m² plan × £90/m² (UK-2026 fabricated + erected; service=structural, dry, 0 bar — NOT a pressure shell) + £8k connections | Rittal VX25 8284.500 | PASS |  | PASS
X-142 | Cable Trays | 1 | 45 | 45 | class_reference | class-reference price (no itemised inputs) | catalogue | 4 | low | Cable Trays | N/A — proprietary assembly / bought-out package, see datasheet | catalogue | Legrand SRFL100G | PASS |  | PASS
X-143 | Overcurrent Protection | 1 | 3 | 3 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Overcurrent Protection | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
I-113 | Leak Detection Sensor | 1 | 30 | 30 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Leak Detection Sensor | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
X-145 | Motor Overload Protection | 1 | 345 | 345 | catalogue | median £647, n=5 | 19%; £121→£345; lifted; corpus; catalogue | 4 | moderate | Motor Overload Protection | N/A — proprietary assembly / bought-out package, see datasheet | catalogue · lifted £121→£345 to the engine corpus p25 (median £647, n=5; line was 19% of median — under-priced vs the engine's own forge-truth reference) | Siemens 3RU2126-4DB0 | PASS |  | PASS
X-146 | Cip System Connections | 1 | 72 | 72 | class_reference | median £74, n=5 | 12%; £9→£72; lifted; corpus; parametric | 4 | low | Cip System Connections | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric · lifted £9→£72 to the engine corpus p25 (median £74, n=5; line was 12% of median — under-priced vs the engine's own forge-truth reference) | TBD (detailed design) | PASS |  | PASS
X-147 | 3 Part Union Fittings | 1 | 9 | 9 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | 3 Part Union Fittings | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | commodity — MPN at procurement | PASS |  | PASS
X-148 | Modular Stack Design | 1 | 15 | 15 | llm_estimate | model estimate (no itemised inputs) | parametric | 5 | low | Modular Stack Design | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
X-149 | Cable Glands | 1 | 2 | 2 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | moderate | Cable Glands | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | Cabletec CG-M20-IP68 | PASS |  | PASS
X-101 | Cip System | 1 | 218 | 218 | class_reference | class-reference price (no itemised inputs) | parametric | 4 | low | Cip System | N/A — proprietary assembly / bought-out package, see datasheet | bottom-up parametric | TBD (detailed design) | PASS |  | PASS
TK-102 / TK-101 | Cip Tank · 1.4 m dia x 1.3 m | 2 | 4000 | 8000 | class_reference | 6 mm; 1.3 m; 13 kPa; 18 MPa; 7 m²; 89 kg; median £8,082, n | ×1.3; × 89; £12.0/kg; × 1.25; 42%; £3,404→£4,000; lifted; | 4 | low | Cleaning Tank · 1.4 m dia x 1.3 m | FRP/GRP | tapered wall 6 mm = P·r/(σ·E)+c · ⌀1.4×1.3 m (open top (no head)) · P=13 kPa head · σ=18 MPa → 7 m² × 89 kg FRP/GRP @ £12.0/kg supply × 1.25 erection + fittings · lifted £3,404→£4,000 to the engine corpus p25 (median £8,082, n=5; line was 42% of median — under-priced vs the engine's own forge-truth reference) | bespoke fabrication to drawing — see sizing basis | PASS |  | PASS
TK-102.1 / TK-101.1 | ↳ Tank Wall (laminate) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.2 / TK-101.2 | ↳ Tank Floor (graded to centre) | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.3 / TK-101.3 | ↳ Dual Drain / Centre Standpipe | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.4 / TK-101.4 | ↳ Side Drain & Overflow | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.5 / TK-101.5 | ↳ Inlet Distribution Ring | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.6 / TK-101.6 | ↳ Internal Flow Baffles | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.7 / TK-101.7 | ↳ Rim Stiffener | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.8 / TK-101.8 | ↳ Access Walkway & Handrail | 1 | incl. in parent | — | class_reference | incl. in parent line |  | 4 | low |  |  |  |  | PASS |  | PASS
TK-102.9 / TK-101.9 | ↳ Internal Gelcoat / Lining | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.10 / TK-101.10 | ↳ Earthing Boss | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
TK-102.11 / TK-101.11 | ↳ Nameplate | 1 | incl. in parent | — | llm_estimate | incl. in parent line |  | 5 | low |  |  |  |  | PASS |  | PASS
X-150 | Isolation Valves | 1 | 95 | 95 | llm_estimate | model estimate (no itemised inputs) | floored; parametric | 5 | low | Isolation Valves | PVC-U / 304 stainless (WRAS) | bottom-up parametric · floored to min credible price · MoC: PVC-U / 304 stainless (WRAS) for potable-water service (WRAS-approved wetted materials) | commodity — MPN at procurement | PASS |  | PASS
C01 | water connection: Gac Softener → Softener Vessel · 14.5 m3/h | 1 | 905 | 905 | pipe £66/m @ DN80 (HDPE/ | 10.8 m; 25 m³; 1.4 m | £66/m; × 10.8; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Gac Softener → Softener Vessel · 14.5 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 10.8 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 10.8 m | PASS |  | PASS
C02 | water connection: Gac Softener → Drain Collection Sump · 45 m3/h | 1 | 911 | 911 | pipe £36/m @ DN32 (HDPE/ | 20.4 m; 5 m³; 1.7 m | £36/m; × 20.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Gac Softener → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.4 m | PASS |  | PASS
C03 | water connection: Uf Module Bank → Ro High Pressure Pump · 11 m3/h | 1 | 1614 | 1614 | pipe £66/m @ DN80 (HDPE/ | 21.5 m; 25 m³; 1.4 m | £66/m; × 21.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Uf Module Bank → Ro High Pressure Pump · 11 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 21.5 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 21.5 m | PASS |  | PASS
C04 | water connection: Uf Module Bank → Drain Collection Sump · 45 m3/h | 1 | 975 | 975 | pipe £36/m @ DN32 (HDPE/ | 22.1 m; 5 m³; 1.7 m | £36/m; × 22.1; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Uf Module Bank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 22.1 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 22.1 m | PASS |  | PASS
C05 | water connection: Ro High Pressure Pump → Reverse Osmosis Skid · 11 m3/h | 1 | 2232 | 2232 | pipe £66/m @ DN80 (HDPE/ | 30.9 m; 25 m³; 1.4 m | £66/m; × 30.9; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Ro High Pressure Pump → Reverse Osmosis Skid · 11 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 30.9 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 30.9 m | PASS |  | PASS
C06 | water connection: Ro High Pressure Pump → Drain Collection Sump · 45 m3/h | 1 | 1443 | 1443 | pipe £36/m @ DN32 (HDPE/ | 35.1 m; 5 m³; 1.7 m | £36/m; × 35.1; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Ro High Pressure Pump → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 35.1 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 35.1 m | PASS |  | PASS
C07 | water connection: Cloth Filter → Gac Filter · 80 m3/h | 1 | 1419 | 1419 | pipe £66/m @ DN80 (HDPE/ | 18.6 m; 25 m³; 1.4 m | £66/m; × 18.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cloth Filter → Gac Filter · 80 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 18.6 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 18.6 m | PASS |  | PASS
C08 | water connection: Cloth Filter → Drain Collection Sump · 45 m3/h | 1 | 1023 | 1023 | pipe £36/m @ DN32 (HDPE/ | 23.5 m; 5 m³; 1.7 m | £36/m; × 23.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cloth Filter → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 23.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 23.5 m | PASS |  | PASS
C09 | water connection: Gac Filter → Uv Disinfection · 90 m3/h | 1 | 1559 | 1559 | pipe £66/m @ DN80 (HDPE/ | 20.7 m; 25 m³; 1.4 m; 45 m³ | £66/m; × 20.7; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Gac Filter → Uv Disinfection · 90 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 20.7 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN80 HDPE/PVC-U pipe, 20.7 m | PASS |  | PASS
C10 | water connection: Gac Filter → Drain Collection Sump · 45 m3/h | 1 | 1243 | 1243 | pipe £36/m @ DN32 (HDPE/ | 29.6 m; 5 m³; 1.7 m | £36/m; × 29.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Gac Filter → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 29.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 29.6 m | PASS |  | PASS
C11 | water connection: Uv Disinfection → Drain Collection Sump · 45 m3/h | 1 | 1176 | 1176 | pipe £36/m @ DN32 (HDPE/ | 27.7 m; 5 m³; 1.7 m | £36/m; × 27.7; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Uv Disinfection → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 27.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 27.7 m | PASS |  | PASS
C12 | water connection: Drain Collection Sump → Drain Water Tank · 45 m3/h | 1 | 601 | 601 | pipe £36/m @ DN32 (HDPE/ | 11.7 m; 5 m³; 1.7 m | £36/m; × 11.7; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Drain Water Tank · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 11.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 11.7 m | PASS |  | PASS
C13 | water connection: Drain Collection Sump → Uv Disinfection · 90 m3/h | 1 | 984 | 984 | pipe £36/m @ DN32 (HDPE/ | 22.4 m; 5 m³; 1.7 m; 45 m³ | £36/m; × 22.4; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Uv Disinfection · 90 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 22.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN32 HDPE/PVC-U pipe, 22.4 m | PASS |  | PASS
C14 | water connection: Drain Collection Sump → Softener Vessel · 14.5 m3/h | 1 | 500 | 500 | pipe £36/m @ DN32 (HDPE/ | 8.9 m; 5 m³; 1.7 m | £36/m; × 8.9; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Softener Vessel · 14.5 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 8.9 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 8.9 m | PASS |  | PASS
C15 | water connection: Drain Collection Sump → Hand Watering Pump · 25 m3/h | 1 | 1236 | 1236 | pipe £36/m @ DN32 (HDPE/ | 29.4 m; 5 m³; 1.7 m | £36/m; × 29.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Hand Watering Pump · 25 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 29.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 29.4 m | PASS |  | PASS
C16 | water connection: Drain Collection Sump → Cloth Filter · 80 m3/h | 1 | 879 | 879 | pipe £36/m @ DN32 (HDPE/ | 19.5 m; 5 m³; 1.7 m | £36/m; × 19.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Cloth Filter · 80 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 19.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 19.5 m | PASS |  | PASS
C17 | water connection: Drain Collection Sump → Gac Softener · 14.5 m3/h | 1 | 516 | 516 | pipe £36/m @ DN32 (HDPE/ | 9.4 m; 5 m³; 1.7 m | £36/m; × 9.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Gac Softener · 14.5 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 9.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 9.4 m | PASS |  | PASS
C18 | water connection: Drain Collection Sump → Irrigation Pump · 90 m3/h | 1 | 1138 | 1138 | pipe £36/m @ DN32 (HDPE/ | 26.7 m; 5 m³; 1.7 m; 45 m³ | £36/m; × 26.7; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Irrigation Pump · 90 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 26.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN32 HDPE/PVC-U pipe, 26.7 m | PASS |  | PASS
C19 | water connection: Drain Collection Sump → Reverse Osmosis Skid · 45 m3/h | 1 | 312 | 312 | pipe £36/m @ DN32 (HDPE/ | 3.7 m; 5 m³; 1.7 m | £36/m; × 3.7; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Reverse Osmosis Skid · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 3.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 3.7 m | PASS |  | PASS
C20 | water connection: Drain Collection Sump → Ro High Pressure Pump · 11 m3/h | 1 | 1273 | 1273 | pipe £36/m @ DN32 (HDPE/ | 30.4 m; 5 m³; 1.7 m | £36/m; × 30.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Ro High Pressure Pump · 11 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 30.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 30.4 m | PASS |  | PASS
C21 | water connection: Drain Collection Sump → Gac Filter · 45 m3/h | 1 | 1041 | 1041 | pipe £36/m @ DN32 (HDPE/ | 24.0 m; 5 m³; 1.7 m | £36/m; × 24.0; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Gac Filter · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 24.0 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 24.0 m | PASS |  | PASS
C22 | water connection: Drain Collection Sump → Uf Module Bank · 45 m3/h | 1 | 487 | 487 | pipe £36/m @ DN32 (HDPE/ | 8.6 m; 5 m³; 1.7 m | £36/m; × 8.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Uf Module Bank · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 8.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 8.6 m | PASS |  | PASS
C23 | water connection: Drain Collection Sump → Cleaning Tank · 4 m3/h | 1 | 909 | 909 | pipe £36/m @ DN32 (HDPE/ | 20.3 m; 5 m³; 1.7 m | £36/m; × 20.3; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Cleaning Tank · 4 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.3 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.3 m | PASS |  | PASS
C24 | water connection: Drain Collection Sump → Cip Tank · 4 m3/h | 1 | 1039 | 1039 | pipe £36/m @ DN32 (HDPE/ | 23.9 m; 5 m³; 1.7 m | £36/m; × 23.9; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Collection Sump → Cip Tank · 4 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 23.9 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 23.9 m | PASS |  | PASS
C25 | water connection: Drain Water Tank → Drain Transfer Pump · 45 m3/h | 1 | 1169 | 1169 | pipe £36/m @ DN32 (HDPE/ | 27.5 m; 5 m³; 1.7 m | £36/m; × 27.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Water Tank → Drain Transfer Pump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 27.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 27.5 m | PASS |  | PASS
C26 | water connection: Drain Transfer Pump → Cip Tank · 4 m3/h | 1 | 1169 | 1169 | pipe £36/m @ DN32 (HDPE/ | 27.5 m; 5 m³; 1.7 m | £36/m; × 27.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Drain Transfer Pump → Cip Tank · 4 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 27.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 27.5 m | PASS |  | PASS
C27 | water connection: Cip Tank → Cleaning Tank · 4 m3/h | 1 | 413 | 413 | pipe £66/m @ DN80 (HDPE/ | 3.3 m; 25 m³; 1.4 m | £66/m; × 3.3; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cip Tank → Cleaning Tank · 4 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 3.3 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 3.3 m | PASS |  | PASS
C28 | water connection: Cip Tank → Drain Collection Sump · 45 m3/h | 1 | 921 | 921 | pipe £36/m @ DN32 (HDPE/ | 20.6 m; 5 m³; 1.7 m | £36/m; × 20.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cip Tank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.6 m | PASS |  | PASS
C29 | water connection: Cleaning Tank → Fresh Water Tank · 4 m3/h | 1 | 678 | 678 | pipe £36/m @ DN32 (HDPE/ | 13.9 m; 5 m³; 1.7 m | £36/m; × 13.9; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cleaning Tank → Fresh Water Tank · 4 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 13.9 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 13.9 m | PASS |  | PASS
C30 | water connection: Cleaning Tank → Drain Collection Sump · 45 m3/h | 1 | 1059 | 1059 | pipe £36/m @ DN32 (HDPE/ | 24.5 m; 5 m³; 1.7 m | £36/m; × 24.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Cleaning Tank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 24.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 24.5 m | PASS |  | PASS
C31 | water connection: Fresh Water Tank → Nutrient Tank · — | 1 | 318 | 318 | pipe £36/m @ DN32 (HDPE/ | 3.9 m; 5 m³; 1.7 m | £36/m; × 3.9; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Nutrient Tank · — | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 3.9 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 3.9 m | PASS |  | PASS
C32 | water connection: Fresh Water Tank → Permeate Outlet · 90 m3/h | 1 | 1069 | 1069 | pipe £36/m @ DN32 (HDPE/ | 24.7 m; 5 m³; 1.7 m; 45 m³ | £36/m; × 24.7; 0.4%; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Permeate Outlet · 90 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 24.7 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN32 HDPE/PVC-U pipe, 24.7 m | PASS |  | PASS
C33 | water connection: Fresh Water Tank → Drain Collection Sump · 45 m3/h | 1 | 1158 | 1158 | pipe £36/m @ DN32 (HDPE/ | 27.2 m; 5 m³; 1.7 m | £36/m; × 27.2; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 27.2 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 27.2 m | PASS |  | PASS
C34 | water connection: Fresh Water Tank → Drain Transfer Pump · 45 m3/h | 1 | 1493 | 1493 | pipe £36/m @ DN32 (HDPE/ | 36.5 m; 5 m³; 1.7 m | £36/m; × 36.5; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Drain Transfer Pump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 36.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 36.5 m | PASS |  | PASS
C35 | water connection: Fresh Water Tank → Drain Water Tank · — | 1 | 897 | 897 | pipe £36/m @ DN32 (HDPE/ | 20.0 m; 5 m³; 1.7 m | £36/m; × 20.0; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fresh Water Tank → Drain Water Tank · — | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.0 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.0 m | PASS |  | PASS
C36 | water connection: Fertigation Dosing Pump → Hand Watering Pump · 25 m3/h | 1 | 1004 | 1004 | pipe £28/m @ DN20 (HDPE/ | 29.6 m; 2 m³; 1.8 m | £28/m; × 29.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fertigation Dosing Pump → Hand Watering Pump · 25 m3/h | HDPE/PVC-U | pipe £28/m @ DN20 (HDPE/PVC-U) × 29.6 m + 2 ends · sized 2 m³/h @ 1.8 m/s · chemical-dosing branch duty · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN20 HDPE/PVC-U pipe, 29.6 m | PASS |  | PASS
C37 | water connection: Fertigation Dosing Pump → Drain Collection Sump · 45 m3/h | 1 | 875 | 875 | pipe £36/m @ DN32 (HDPE/ | 19.4 m; 5 m³; 1.7 m | £36/m; × 19.4; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Fertigation Dosing Pump → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 19.4 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 19.4 m | PASS |  | PASS
C38 | water connection: Hand Watering Pump → Irrigation Pump · 90 m3/h | 1 | 625 | 625 | pipe £66/m @ DN80 (HDPE/ | 6.5 m; 25 m³; 1.4 m; 45 m³ | £66/m; × 6.5; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Hand Watering Pump → Irrigation Pump · 90 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 6.5 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) · demand-sized: peak irrigation demand = 45 m³/h per department × 2 departments | DN80 HDPE/PVC-U pipe, 6.5 m | PASS |  | PASS
C39 | water connection: Hand Watering Pump → Drain Collection Sump · 45 m3/h | 1 | 1384 | 1384 | pipe £36/m @ DN32 (HDPE/ | 33.5 m; 5 m³; 1.7 m | £36/m; × 33.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Hand Watering Pump → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 33.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 33.5 m | PASS |  | PASS
C40 | water connection: Irrigation Pump → Distribution Manifold · 45 m3/h | 1 | 406 | 406 | pipe £104/m @ DN125 (HDP | 1.9 m; 60 m³; 1.4 m | £104/m; × 1.9; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Irrigation Pump → Distribution Manifold · 45 m3/h | HDPE/PVC-U | pipe £104/m @ DN125 (HDPE/PVC-U) × 1.9 m + 2 ends · sized 60 m³/h @ 1.4 m/s · distribution/header branch duty · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN125 HDPE/PVC-U pipe, 1.9 m | PASS |  | PASS
C41 | water connection: Irrigation Pump → Drain Collection Sump · 45 m3/h | 1 | 1296 | 1296 | pipe £36/m @ DN32 (HDPE/ | 31.1 m; 5 m³; 1.7 m | £36/m; × 31.1; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Irrigation Pump → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 31.1 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 31.1 m | PASS |  | PASS
C42 | electrical connection: Mains Incomer → Standby Diesel Generator · 4.2 A | 1 | 43 | 43 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Mains Incomer → Standby Diesel Generator · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 10.2 m | PASS |  | PASS
C43 | electrical connection: Standby Diesel Generator → Transformer · 4.2 A | 1 | 37 | 37 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Standby Diesel Generator → Transformer · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 8.4 m | PASS |  | PASS
C44 | electrical connection: Transformer → Main Switchboard · 4.2 A | 1 | 30 | 30 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Transformer → Main Switchboard · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 5.9 m | PASS |  | PASS
C45 | electrical connection: Main Switchboard → Motor Control Center · 4.2 A | 1 | 72 | 72 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Main Switchboard → Motor Control Center · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 20.0 m | PASS |  | PASS
C46 | electrical connection: Motor Control Center → 3 Phase Power Input · 4.2 A | 1 | 29 | 29 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → 3 Phase Power Input · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 5.7 m | PASS |  | PASS
C47 | electrical connection: Motor Control Center → Piping Network · 4.2 A | 1 | 90 | 90 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Piping Network · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 25.8 m | PASS |  | PASS
C48 | electrical connection: Motor Control Center → Uv Disinfection · 8.2 A | 1 | 87 | 87 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Uv Disinfection · 8.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 24.9 m | PASS |  | PASS
C49 | electrical connection: Motor Control Center → Fertigation Dosing Pump · 15 A | 1 | 83 | 83 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Fertigation Dosing Pump · 15 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 23.7 m | PASS |  | PASS
C50 | electrical connection: Motor Control Center → Hand Watering Pump · 4.2 A | 1 | 106 | 106 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Hand Watering Pump · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 31.2 m | PASS |  | PASS
C51 | electrical connection: Motor Control Center → Drain Transfer Pump · 3.9 A | 1 | 94 | 94 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Drain Transfer Pump · 3.9 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 27.3 m | PASS |  | PASS
C52 | electrical connection: Motor Control Center → Cloth Filter · 4.2 A | 1 | 76 | 76 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Cloth Filter · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 21.2 m | PASS |  | PASS
C53 | electrical connection: Motor Control Center → Irrigation Pump · 4.2 A | 1 | 96 | 96 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Irrigation Pump · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 28.0 m | PASS |  | PASS
C54 | electrical connection: Motor Control Center → Ro High Pressure Pump · 8.4 A | 1 | 109 | 109 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Ro High Pressure Pump · 8.4 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 32.4 m | PASS |  | PASS
C55 | electrical connection: Motor Control Center → Gac Filter · 4.2 A | 1 | 113 | 113 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Gac Filter · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 33.7 m | PASS |  | PASS
C56 | electrical connection: Motor Control Center → Permeate Outlet · 4.2 A | 1 | 44 | 44 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Permeate Outlet · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 10.5 m | PASS |  | PASS
C57 | electrical connection: Motor Control Center → Concentrate Outlet · 4.2 A | 1 | 35 | 35 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Concentrate Outlet · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 7.5 m | PASS |  | PASS
C58 | water connection: Ultrafiltration Module → Fresh Water Tank · 1.35 m3/h | 1 | 920 | 920 | pipe £36/m @ DN32 (HDPE/ | 20.6 m; 5 m³; 1.7 m | £36/m; × 20.6; 0.4%; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Ultrafiltration Module → Fresh Water Tank · 1.35 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 20.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · make-up water duty (~0.4% of recirc) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 20.6 m | PASS |  | PASS
C59 | water connection: Permeate Outlet → Cip Tank · 4 m3/h | 1 | 3161 | 3161 | pipe £66/m @ DN80 (HDPE/ | 45.0 m; 25 m³; 1.4 m | £66/m; × 45.0; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Permeate Outlet → Cip Tank · 4 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 45.0 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 45.0 m | PASS |  | PASS
C60 | water connection: Permeate Outlet → Ultrafiltration Module · 8 m3/h | 1 | 1594 | 1594 | pipe £66/m @ DN80 (HDPE/ | 21.2 m; 25 m³; 1.4 m | £66/m; × 21.2; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Permeate Outlet → Ultrafiltration Module · 8 m3/h | HDPE/PVC-U | pipe £66/m @ DN80 (HDPE/PVC-U) × 21.2 m + 2 ends · sized 25 m³/h @ 1.4 m/s · branch duty (default — endpoint not on main loop) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN80 HDPE/PVC-U pipe, 21.2 m | PASS |  | PASS
C61 | water connection: Softener Vessel → Drain Collection Sump · 45 m3/h | 1 | 447 | 447 | pipe £36/m @ DN32 (HDPE/ | 7.5 m; 5 m³; 1.7 m | £36/m; × 7.5; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Softener Vessel → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 7.5 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 7.5 m | PASS |  | PASS
C62 | water connection: Nutrient Tank → Drain Collection Sump · 45 m3/h | 1 | 1316 | 1316 | pipe £36/m @ DN32 (HDPE/ | 31.6 m; 5 m³; 1.7 m | £36/m; × 31.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Nutrient Tank → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 31.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 31.6 m | PASS |  | PASS
C63 | water connection: Distribution Manifold → Drain Collection Sump · 45 m3/h | 1 | 1352 | 1352 | pipe £36/m @ DN32 (HDPE/ | 32.6 m; 5 m³; 1.7 m | £36/m; × 32.6; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Distribution Manifold → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 32.6 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 32.6 m | PASS |  | PASS
C64 | water connection: Reverse Osmosis Skid → Drain Collection Sump · 45 m3/h | 1 | 604 | 604 | pipe £36/m @ DN32 (HDPE/ | 11.8 m; 5 m³; 1.7 m | £36/m; × 11.8; install | 3 | moderate — deterministic take-off (routed length × rate) | water connection: Reverse Osmosis Skid → Drain Collection Sump · 45 m3/h | HDPE/PVC-U | pipe £36/m @ DN32 (HDPE/PVC-U) × 11.8 m + 2 ends · sized 5 m³/h @ 1.7 m/s · bleed/drain duty (~make-up balance) · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | DN32 HDPE/PVC-U pipe, 11.8 m | PASS |  | PASS
C65 | electrical connection: Motor Control Center → Electrical Control Panel · 4.2 A | 1 | 23 | 23 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Electrical Control Panel · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 3.6 m | PASS |  | PASS
C66 | electrical connection: Electrical Control Panel → Digital Control Panel · 0.5 A | 1 | 21 | 21 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Electrical Control Panel → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 2.9 m | PASS |  | PASS
C67 | electrical connection: Motor Control Center → Control + Instrument UPS · 4.2 A | 1 | 23 | 23 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Control + Instrument UPS · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 3.6 m | PASS |  | PASS
C68 | electrical connection: Control + Instrument UPS → Digital Control Panel · 0.5 A | 1 | 19 | 19 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Control + Instrument UPS → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 2.5 m | PASS |  | PASS
C69 | electrical connection: Motor Control Center → SCADA / Plant Control System · 4.2 A | 1 | 22 | 22 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → SCADA / Plant Control System · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 3.6 m | PASS |  | PASS
C70 | electrical connection: Motor Control Center → Digital Control Panel · 0.5 A | 1 | 23 | 23 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 3.5 m | PASS |  | PASS
C71 | electrical connection: Piping Network → Digital Control Panel · 0.5 A | 1 | 93 | 93 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Piping Network → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 27.0 m | PASS |  | PASS
C72 | electrical connection: Motor Control Center → Electrical Control Cabinet · 4.2 A | 1 | 96 | 96 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Electrical Control Cabinet · 4.2 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 28.0 m | PASS |  | PASS
C73 | electrical connection: Electrical Control Cabinet → Digital Control Panel · 0.5 A | 1 | 96 | 96 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Electrical Control Cabinet → Digital Control Panel · 0.5 A | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | 1 × 1.5 mm² Cu, 27.9 m | PASS |  | PASS
C74 | electrical connection: Motor Control Center → Digital Control Panel · — | 1 | 23 | 23 | cable £3/m | 1.5 mm | £3/m·conductor; × 1; ×1; £6/end; × 2; install | 3 | moderate — deterministic take-off (routed length × rate) | electrical connection: Motor Control Center → Digital Control Panel · — | Cu conductor, LSZH/XLPE insulated (BS 6724/BS 5467 class) | cable £3/m·conductor @ 1.5 mm² × 1 conductor(s) (1∥×1 core) + £6/end-lug × 2 ends · installed cost — supply + installation labour + terminations included (uk-2026 supply+install model; not a bare-fittings/component price) | power feeder, 3.8 m (design current unknown) | PASS |  | PASS
X-151 | Zoned distribution — department delivery mains · DN125 PVC-U · 214 m | 214 | 20.8 | 4451 | parametric | 214 m; 7.7 m; 30 m; 45 m³; 1.3 m; 90 m³ | £20.8/m; 20%; £104/m; × 7.7; × 30; × 5; install; parametri |  |  | Zoned distribution — department delivery mains · DN125 PVC-U · 214 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 214 m × £20.8/m supply-only materials (20% of the uk-2026 supply+install £104/m @ DN125; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): delivery mains (department spines) = 2 group(s) × (10 branches × 7.7 m branch pitch + 30 m plant-room stand-off) = 214 m; DN125 at 45 m³/h ≤ 1.3 m/s (surge-limited delivery main on a cycling valve network) · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN125 PVC-U pressure pipe + fittings + hangers, 214 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-152 | Zoned distribution — department delivery mains · DN125 PVC-U · 280 m | 280 | 20.8 | 5824 | parametric | 280 m; 7 m; 1.3 m; 0.5 m; 45 m³; 90 m³ | £20.8/m; 20%; £104/m; × 7; × 1.3; × 30; × 5; install; para |  |  | Zoned distribution — delivery risers · DN125 PVC-U · 280 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 280 m × £20.8/m supply-only materials (20% of the uk-2026 supply+install £104/m @ DN125; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): delivery risers = 40 risers (200 zones ÷ 5 levels) × 7 m (5 levels × 1.3 m tier pitch + 0.5 m) = 280 m; DN125 at 45 m³/h ≤ 1.3 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN125 PVC-U pressure pipe + fittings + hangers, 280 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-153 | Zoned distribution — department delivery mains · DN75 PVC-U · 8,280 m | 8280 | 13.2 | 109296 | parametric | 8,280 m; 2.76 m; 41.4 m; 8280 m; 45 m³; 3.0 m; 90 m³ | £13.2/m; 20%; £66/m; × 2.76; × 41.4; × 30; × 5; install; p |  |  | Zoned distribution — zone laterals (flood-fill lines) · DN75 PVC-U · 8,280 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 8,280 m × £13.2/m supply-only materials (20% of the uk-2026 supply+install £66/m @ DN75; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): zone laterals = 200 zones × (30 positions/zone ÷ 2 rows × 2.76 m position pitch) = 200 × 41.4 m = 8280 m; DN75 at the 45 m³/h open-zone flood-fill duty ≤ 3.0 m/s (short-duration fill) · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN75 PVC-U pressure pipe + fittings + hangers, 8,280 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-154 | Zoned distribution — department delivery mains · DN110 PVC-U · 4,200 m | 4200 | 20.8 | 87360 | parametric | 4,200 m; 7 m; 4200 m; 45 m³; 1.4 m; 90 m³ | £20.8/m; 20%; £104/m; × 7; × 30; × 5; install; parametric |  |  | Zoned distribution — drain/return risers (gravity) · DN110 PVC-U · 4,200 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 4,200 m × £20.8/m supply-only materials (20% of the uk-2026 supply+install £104/m @ DN110; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): drain/return risers (mirror of the delivery grid) = 600 gravity drops (an outlet per 2 positions per level) × 7 m = 4200 m; DN110 gravity at 45 m³/h ≤ 1.4 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN110 PVC-U pressure pipe + fittings + hangers, 4,200 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-155 | Zoned distribution — department delivery mains · DN110 PVC-U · 1,656 m | 1656 | 20.8 | 34445 | parametric | 1,656 m; 41.4 m; 1656 m; 1.4 m; 45 m³; 90 m³ | £20.8/m; 20%; £104/m; × 41.4; × 20; × 30; × 5; install; pa |  |  | Zoned distribution — drain collection lines · DN110 PVC-U · 1,656 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 1,656 m × £20.8/m supply-only materials (20% of the uk-2026 supply+install £104/m @ DN110; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): drain collection lines = 2 floor lines/branch × 41.4 m × 20 branches = 1656 m; DN110 gravity ≤ 1.4 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN110 PVC-U pressure pipe + fittings + hangers, 1,656 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-156 | Zoned distribution — department delivery mains · DN160 PVC-U · 214 m | 214 | 35.2 | 7533 | parametric | 214 m; 45 m³; 0.8 m; 90 m³ | £35.2/m; 20%; £176/m; × 30; × 5; install; parametric |  |  | Zoned distribution — main drain headers · DN160 PVC-U · 214 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network (engineered allowance, NOT per-pipe routed; client distribution-section scope): 214 m × £35.2/m supply-only materials (20% of the uk-2026 supply+install £176/m @ DN160; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): main drain headers = the delivery-spine mirror (214 m); DN160 at 45 m³/h ≤ 0.8 m/s part-full gravity equivalent · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN160 PVC-U pressure pipe + fittings + hangers, 214 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-157 | Hand watering — ring main to both departments · DN90 PVC-U · 428 m | 428 | 16.4 | 7019 | parametric | 428 m; 107 m; 45 m³; 90 m³ | £16.4/m; 20%; £82/m; × 2; × 30; × 5; install; parametric |  |  | Hand watering — ring main to both departments · DN90 PVC-U · 428 m | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — client section E scope (hand-watering ring main — engineered allowance, NOT per-pipe routed): 428 m × £16.4/m supply-only materials (20% of the uk-2026 supply+install £82/m @ DN90; installation labour is carried by the cost-stack field-install factors — no double count) · length-priced: qty = the run length in metres, unit = £/m · derivation: parametric — not routed (zoned-delivery distribution network, engineered allowance): hand-watering ring main = 2 delivery group(s)/department(s) × 2 legs (ring out-and-return along the 107 m delivery spine, serving every branch head) = 428 m · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | DN90 PVC-U pressure pipe + fittings + hangers, 428 m (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-158 | Zoned distribution — department delivery mains · 6,000 off | 6000 | 6 | 36000 | parametric | parametric estimate (no itemised inputs) | parametric |  |  | Zoned distribution — delivery inlet stubs, one per served position · 6,000 off | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network: 6,000 served positions × £6 inlet-stub materials allowance (tee + stub + inlet fitting, ex-works) · parametric — not routed (zoned-delivery distribution network, engineered allowance): one delivery inlet stub + fitting per served position = 6000 | Small-bore PVC-U tee + stub + inlet fitting (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
X-159 | Zoned distribution — department delivery mains · 3,000 off | 3000 | 9 | 27000 | parametric | parametric estimate (no itemised inputs) | parametric |  |  | Zoned distribution — drain outlet connections (one per 2 positions) · 3,000 off | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network: 3,000 drain outlets × £9 gravity tee/branch materials allowance (ex-works) · parametric — not routed (zoned-delivery distribution network, engineered allowance): one gravity drain outlet per 2 served positions = 3000 | PVC-U gravity tee/branch outlet fitting (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
V-112 | Zoned distribution — department delivery mains · 200 off | 200 | 40 | 8000 | parametric | parametric estimate (no itemised inputs) | parametric |  |  | Zoned distribution — zone valve connection kits · 200 off | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — zoned-delivery distribution network: 200 valve zones × £40 connection-kit materials allowance; the actuated valve assemblies themselves are priced on their own BoM line (assembly family £/DN) — this kit is the pipework tie-in only, no double count · parametric — not routed (zoned-delivery distribution network, engineered allowance): one zone connection kit (valve stub-in, unions, supports) per sectioning valve = 200 | Zone valve stub-in: unions, supports, riser tie-in (supply; valve body + actuator priced on the actuated-valve assembly line) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
V-113 | Hand watering — ring main to both departments · 44 off | 44 | 45 | 1980 | parametric | parametric estimate (no itemised inputs) | × 20; install; parametric |  |  | Hand watering — tap/hose stations (riser, hand valve + quick connector) · 44 off | PVC-U (thermoplastic pressure pipework, solvent-weld) | parametric estimate — client section E scope (hand-watering ring main — engineered allowance, NOT per-pipe routed): 44 tap/hose stations × £45 per-station materials allowance (brass hand valve ~£14 + quick-release hose coupler ~£9 + ring-main tee, riser stub + clamps ~£22, ex-works; installation labour is carried by the cost-stack field-install factors — no double count) · parametric — not routed (zoned-delivery distribution network, engineered allowance): hand-watering tap risers (each a hand valve + quick connector) = 2 per branch × 20 branches + 2 per delivery group at the plant/irrigation room (4) = 44 | Ring-main riser stub-in: brass hand valve, quick-release hose coupler, tee + clamps (supply) | PASS |  | ⚠ FAIL — 'Est class' empty; 'Confidence' empty
Σ TOTAL |  |  |  | 808885
Coverage by drawing (parts-ledger.json)
Drawing | Expected | Present | % present | [10 empty] | Cell check
blender | 30 | 29 | 96.7 | [10 empty] | PASS
general-arrangement | 30 | 29 | 96.7 | [10 empty] | PASS
pid | 42 | 38 | 90.5 | [10 empty] | PASS
single-line-diagram | 12 | 12 | 100 | [10 empty] | PASS
panel-schedule | 23 | 20 | 87 | [10 empty] | PASS
block-flow-diagram | 18 | 16 | 88.9 | [10 empty] | PASS
process-schedules | 24 | 18 | 75 | [10 empty] | PASS
parts-ledger grand_total_gbp |  |  |  | 808885 | Compare against the LIVE Σ line £ at row 419. See the ⚠ Checks tab for the reconciliation row.

## Brief
Brief — original vs engine-enhanced |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · client-offer reconciliation (live section mapping) — client-offer reconciliation sections consistent (incl. decision-covered) 6/6; every live section rendered as a recon… · full audit: Quality & Audit tab
The verbatim client brief (left) and the engine's structured, enhanced interpretation (right) that drives the whole design.
Original brief (verbatim) | Engine-enhanced brief (structured)
Water, Fertigation and Ebb/Flow Irrigation Plant — Indoor Multi-Layer Cultivation Facility | Product summary
We are designing and specifying a complete water-handling, purification, fertigation and ebb/flow irrigation plant that supplies a large indoor multi-layer cultivation facility. The deliverable is the WATER SYSTEM ONLY — the purification train, the water storage, the nutrient-dosing (fertigation) units, the flood-and-drain (ebb/flow) distribution network, the drain-water recovery, a hand-watering ring main, and the irrigation/fertigation process-control computer. This is a process and fluid-handling plant: pumps, pipes, tanks, reverse osmosis, filtration, valves and dosing. The grow-lighting, the climate/heating-ventilation/cooling hardware, the cultivation rack framework and the building are NOT part of this plant — they are supplied by others and are explicitly out of scope. This is modelled on a real turnkey supplier offer (a specialist water-systems supplier, 2020) totalling €1,395,019. | Automated water purification, storage, and nutrient-dosing (fertigation) plant for indoor controlled-environment agriculture.
Target market: indoor and vertical-farming operators, controlled-environment-agriculture growers, glasshouse and horticulture operators across the United Kingdom and Europe who need a turnkey water-treatment, fertigation and irrigation plant for a multi-layer growing facility.
System description (the six delivered subsystems): | Primary product
A. WATER PURIFICATION — treats incoming potable mains water to the feed quality the growing system needs. | Precisely dosed nutrient-rich irrigation water (fertigation water)
​- Reverse-osmosis unit: hourly permeate capacity 8.0 cubic metres per hour, raw-tap-water blending capacity 1.2 to 1.6 cubic metres per hour, recovery factor 75 percent, working pressure 10.6 bar at 15 degrees Celsius feed, minimum inlet pressure 2.1 bar, water supply required at least 10.7 cubic metres per hour, electrical supply 3 by 400 volt plus neutral 50 hertz, total installed 5.5 kilowatts, consumption 4.2 kilowatts; stainless-steel supporting frame with inlet section, pre-filter set, frequency-controlled high-pressure pump, integrated permeate flushing line, a first-water flush, the membranes in high-pressure lines, and a central programmable-logic-controller panel for fully automatic operation. Water-supply connection DN63 polyvinyl-chloride, reject/waste connection DN50, permeate connection DN50.
​- Particle filter: one 80-micron cleanable particle filter in the inlet line of the carbon filter, distributor with 2-inch connections, transparent housing. | Construction materials
​- Granular-activated-carbon filter: nominal filtration capacity 14.5 cubic metres per hour, one 42-inch tank, pressure drop about 0.5 bar, DN80 connections. | Polyvinyl chloride (PVC) piping, stainless steel frames/pumps, galvanized steel main tanks, FRP pressure vessels, and polyethylene/polyester chemical tanks
​- Water softener: capacity 14.0 cubic metres per hour, minimum 1.75 cubic metres per hour per softener tank, two glass-fibre-reinforced-plastic softener tanks with food-quality strong-acid cation resin (350 litres of resin per tank), automatic brine regeneration with one polyethylene brine vessel holding 355 kilograms of salt; 91 cubic metres treated between regenerations, 35 to 88 kilograms of salt and 2.8 cubic metres of water per regeneration, hardness reduction to 0.1 degrees of hardness or better, 15 watts in operation.
​- Raw-tap-water blending line: adjustable valve and flow indicator on the carbon-filter outlet to blend plus or minus 15 percent of the permeate capacity back into the produced water. | Derived requirements
​- Connection lines: a DN63 polyvinyl-chloride city-water line to the reverse-osmosis unit (within 50 metres), a DN50 polyvinyl-chloride waste line to the sewer, and a DN63 polyvinyl-chloride fresh-water line from the reverse-osmosis unit to the fresh-water tank (within 50 metres). | • RO Permeate Production Capacity: 8 m3/h (stated)
B. WATER STORAGE — galvanised Class-A storage tanks with wall-protection blanket, a 0.6-millimetre black anti-algae liner and a duplex polyurethane-coated lowest ring, set on concrete tiles. | • RO Feed Water Demand: 10.7 m3/h (stated)
​- One fresh-water tank, 3.64 metres diameter by 3.88 metres high, 40 cubic metres. | • RO Reject/Waste Flow: 2.7 m3/h (derived)
​- Two drain-water tanks, 3.64 metres diameter by 3.88 metres high, 40 cubic metres each. | • Total Fresh Water Production (Blended): 9.6 m3/h (derived)
​- Level monitoring: a 4-channel level processor with one pressure sensor per tank. | • Total Irrigation Pumping Capacity: 90 m3/h (derived)
​- Suction lines: DN110 polyvinyl-chloride from the fresh-water tank to the hand-watering unit; DN160 polyvinyl-chloride suction lines from the fresh-water tank to each of the two fertiliser units and from each drain-water tank to its fertiliser unit; each with a butterfly valve and a bottom connection. | • Fertigation Delivery Pressure: 3.5 bar (stated)
C. FERTILISER (FERTIGATION) UNITS — two A/B nutrient-dosing units, each 45 cubic metres per hour, for the multi-layer ebb/flow system, dosing the A and B fertiliser streams simultaneously by suction. Each unit consists of: | • Total Water Storage Capacity: 120 m3 (stated)
​- a stainless-steel frame with adjustable supports; | • Nutrient Stock Storage Capacity: 8000 L (derived)
​- two 125-millimetre Keystone Composeal manual butterfly valves and two 125-millimetre check valves; | • Minimum Softener Regeneration Cycle Time: 8.5 h (derived)
​- one double-action electrically-operated 125-millimetre Keystone Composeal valve for reusing drain water, with an electrical-conductivity supply measuring sensor; | • Softener Salt Consumption per Regeneration: 88 kg (stated)
​- one Lowara e-SHE 50-160/75 circulation pump, 7.5 kilowatts, 45 cubic metres per hour at 3.5 bar, with thermostat and polyvinyl-chloride flanges; | • Major Equipment Installed Electrical Load: 20.5 kW (derived)
​- one 0-to-10-bar pressure sensor for the frequency controller; | • Particle Filtration Limit: 80 microns (stated)
​- an A-B dosing system on the simultaneous-suction principle: a stainless-steel motorised control unit, two polyvinyl-chloride venturi injectors, two flowmeters, two membrane control valves, and two shunt lines on the pump suction/discharge; | • Hand Watering Capacity: 25 m3/h (stated)
​- an electrical-conductivity / pH measuring shunt (110-millimetre, Hoogendoorn): a bypass line with a 25-millimetre tube, two ball valves, and electrical-conductivity and pH sensors;
​- one acid dosing pump (Iwaki EWN-C21VCER) with a 100-litre barrel, and one chemical dosing pump (Iwaki EWN-C21VHERA) with a 100-litre barrel; | Operating conditions
​- one 90-millimetre paddle-wheel flowmeter and one 110-millimetre check valve. | • ro_feed_water_temperature: 15 C (stated)
Each unit has a pump switch panel (main switch, magnet switch, thermal protection, control/alarm relays, manual start, indication lamps, acoustic and free-potential alarm, Danfoss frequency controller). Nutrient stock: eight 1,000-litre polyester fertiliser tanks (four A, four B) with hinged covers and suction sets, and eight electric mixers on stainless-steel frames. | • electrical_supply: 400V, 3-phase, 50Hz (stated)
D. EBB/FLOW (FLOOD-AND-DRAIN) IRRIGATION INSTALLATION — the flood-and-drain distribution and drain network for the cultivation containers. | • ro_working_pressure: 10.6 bar (stated)
​- Layout: 2 departments, 10 cultivation tunnels per department, 5 layers per tunnel, 4 rows per layer, 15 containers per row — 6,000 cultivation containers total, each 2,760 by 1,290 millimetres; flood depth 15 millimetres; one inlet per container at 1.5 cubic metres per hour; 30 containers per valve, 200 electrically-actuated valves; one valve per department open at a time, giving a maximum demand of 45 cubic metres per hour per department. | • minimum_inlet_pressure: 2.1 bar (stated)
​- Mainlines: DN125 polyvinyl-chloride main line from each fertiliser unit to its department, with two riser connections per tunnel.
​- Risers, valves, distribution: two DN125 risers per cultivation room, each riser fitted with five 2.5-inch electric valves; each valve section feeds 30 containers (two rows of 15) via a DN75 distribution line running the length of the tunnel, with an inlet to each container. | Notes
​- Drain lines: a DN110 outlet per two containers to a DN110 riser (five outlets per riser, one per layer), 15 risers per tunnel side to a DN110 floor drain line, collected into a DN160 main drain line per compartment running to the drain pit. | The system is a fluid-handling and dosing plant for agriculture, not a chemical solvent recovery plant. The 'closed-loop solvent/reagent recovery' mentioned in the prompt's stated process is a misclassification of the ebb/flow drain-water recovery system, which captures and reuses irrigation runoff. Electrical load derived only accounts for major motive power; a diversity factor and minor loads (dosing pumps, sensors, PLC) must be added for main panel sizing.
​- Drain-water pit: a 5,000-litre drain pit per cultivation room with a 45-cubic-metre-per-hour submersible pump discharging through a DN110 line to the cloth filter.
​- Cloth-filter unit: an 80-cubic-metre-per-hour cloth filter per cultivation room on a high-density-polyethylene tank, with a self-priming 45-cubic-metre-per-hour pump returning the filtered drain water to the drain-water tank for reuse.
E. HAND-WATERING INSTALLATION — a frequency-controlled pump, 25 cubic metres per hour at 3.0 bar, on a stainless-steel frame, feeding a DN90 polyvinyl-chloride hand-watering ring main to both departments with 44 risers (two per tunnel plus four at the irrigation room), each with a hand valve and a quick connector.
F. PROCESS-CONTROL COMPUTER — a horticultural irrigation/fertigation process computer (Hoogendoorn iSii class) managing the irrigation scheduling, the closed-loop electrical-conductivity and pH correction, level and flow monitoring, and the safety and fault alarms. Hardware: the process computer in a cabinet, two monitors, a 750-volt-ampere uninterruptible power supply, a radiation sensor, an Ethernet-CAN interface, and 22 distributed datapoint input/output casings. Water hardware: two pulse/litre counters, two inductive electrical-conductivity sensors and transmitters, two pH sensors, two pH transmitters, two pH-sensor armatures. Bus terminals: 4-channel digital-input, 4-to-20-milliamp and 0-to-20-milliamp analogue-input, and 55 four-channel digital-output AC/DC terminals. Software functions: two irrigation units with pump, 200 valves, two electrical-conductivity controls, two pH controls, two pH checks, two 16-choice fertiliser-selection groups, 20 crop sections, 20 registration groups, 20 recipes. Control cabling: control-bus and multi-core signal cable runs (500 to 2,000 metres each).
Key constraints (the brief's target metrics):
​- Total cultivation containers (trays): approximately 6,000 (the irrigation network sizing driver)
​- Maximum irrigation demand: approximately 45 cubic metres per hour per department (two departments)
​- Reverse-osmosis permeate capacity: approximately 8 cubic metres per hour at approximately 75 percent recovery
​- Granular-activated-carbon and softener throughput: approximately 14 to 14.5 cubic metres per hour
​- Water-storage capacity: three tanks of approximately 40 cubic metres each (one fresh, two drain)
​- Fertigation: two A/B dosing units of approximately 45 cubic metres per hour, each with an approximately 7.5-kilowatt circulation pump at approximately 3.5 bar, closed-loop electrical-conductivity and pH correction, and eight 1,000-litre nutrient stock tanks (four A, four B)
​- Hand watering: approximately 25 cubic metres per hour at approximately 3 bar
​- Pipework: thermoplastic (polyvinyl-chloride) pressure pipework throughout, DN50 to DN160, sized for the stated flows
​- Electrical supply: 400 volt, three-phase, 50 hertz; the design must state the connected and average electrical load (the plant is pumps, dosing and controls — of the order of low tens of kilowatts, NOT megawatts)
​- Number of actuated valves: approximately 200
​- Design life: 20 years
​- Annual production volume: 6 units per year
​- Unit cost ceiling: approximately £1,250,000 to £1,400,000 installed for the water, storage, fertigation, irrigation and control plant
​- Primary objective: balanced — the lowest installed cost that meets the irrigation throughput, the water-purity and the layout targets
Cost and calibration context (the reference supplier offer — the ground truth the engine must reproduce):
​- A. Water purification: approximately £85,000 (€94,735)
​- B. Water storage: approximately £31,000 (€34,553)
​- C. Fertiliser/fertigation units: approximately £92,000 (€102,234)
​- D. Ebb/flow irrigation installation: approximately £895,000 (€993,750) — the dominant cost, overwhelmingly installed polyvinyl-chloride pipework, the approximately 200 actuated valves, the risers and the drain network, plus installation labour, NOT major equipment
​- E. Hand watering: approximately £24,000 (€26,857)
​- F. Process-control computer: approximately £128,000 (€142,890)
​- Total: approximately £1,250,000 (€1,395,019)
​- The ebb/flow irrigation network (D) is roughly 71 percent of the total, so the bill of materials and the cost build-up must capture the long pipe runs, the approximately 200 actuated valves, the risers and the drain network — not just the major equipment.
Safety and regulatory:
​- Pressure Systems Safety Regulations for the pressurised vessels and the reverse-osmosis high-pressure section
​- Control of Substances Hazardous to Health assessment for the acid and concentrated-nutrient dosing chemicals (corrosive; segregated bunded storage, eyewash and personal protective equipment)
​- Water Supply (Water Fittings) Regulations and backflow prevention on the mains connection (Fluid Category protection)
​- Machinery Directive, Low Voltage Directive and Electromagnetic Compatibility Directive for the equipment
​- Legionella / water-hygiene control on the stored and recirculated water
​- UKCA marking
Explicitly EXCLUDED (out of scope — supplied by others, per the supplier exemptions):
​- the grow-lighting / assimilation lighting and its switchboards
​- the climate / heating, ventilation and cooling hardware and the climate-control computer
​- the cultivation rack framework
​- the building, civil works and excavation
​- the main electrical switchboard and the feeder cables to it, and earthing/cable tray/cable penetrations
Sub-modules expected: mains water intake and backflow protection, water softening, granular-activated-carbon filtration, particle filtration, reverse-osmosis purification and blending, fresh-water and drain-water storage with level monitoring, A/B nutrient dosing and electrical-conductivity/pH correction, nutrient stock-tank storage and mixing, ebb/flow distribution mains/risers/actuated valve sections, gravity drain collection and drain pit, drain-water cloth filtration and return, hand-watering ring main, irrigation/fertigation process-control and instrumentation, and the control cabling.
Client offer vs this design, by subsystem
Mapping: each BoM line is classed to a client section by its SERVICE/SCOPE family — the MOST SPECIFIC subsystem keyword match wins (ties in the client's own A→F order); an interconnect line follows its service (electrical/control cabling → the controls section; pipework touching the distribution/drain network → that section; other process runs → their source endpoint's section); plant-wide field instrumentation → the controls-and-instrumentation section. Each row states WHICH line families it counted. Unallocated lines are shown separately, NEVER forced into a match, and Σ sections + unallocated equals the bill total EXACTLY (asserted at build). The client's section prices are INSTALLED, so the comparison column is the engine installed-equivalent = section BoM materials × 1.7 (this run's installed ÷ materials ratio from the cost stack). Recorded scope decisions (briefs-loop/water-treatment-example.decisions.json) render inline: a diverging section covered by a decision reads CONSISTENT WITH RECORDED DECISION (who/date/rationale + the real numbers); a diverging section with NO recorded decision still fails.
Client section | Client offer £ (installed) | This design £ (BoM materials) | Installed-equivalent £ | Δ vs offer £ | Honest note | Cell check
A. Water purification | 85000 | 117020 | 198934 | 113934 | CONSISTENT WITH RECORDED DECISION — engine 2.3× the client section (installed-equiv £198,934 vs client £85,000). The engine's fuller purification design stands versus the leaner client offer — accepted scope, not a defect to tune away. — Tristan Fischer, 2026-07-03. Rationale: The engine includes an ultrafiltration membrane bank, ultraviolet disinfection and duplicated granular-activated-carbon/softener treatment trains that the client's offer never priced; the whole-plant total remains ~1.1x the client's GBP 1,250,000 offer. [evidence: engine installed-equivalent ~2.3x the client section (v61: GBP 198,958 vs GBP 85,000); whole-plant total 1.11x] · COUNTED: 12× section scope stems (most-specific match) £105,035 · 7× process interconnect (by source endpoint) £11,985 | PASS
B. Water storage | 31000 | 43807 | 74472 | 43472 | CONSISTENT WITH RECORDED DECISION — engine 2.4× the client section (installed-equiv £74,472 vs client £31,000). The engine's fuller tank scope stands versus the leaner client offer — accepted scope, not a defect to tune away. — Tristan Fischer, 2026-07-03. Rationale: The engine prices fuller installed tank scope (~GBP 23k per installed 40 m3 galvanised tank vs the client's ~GBP 10k) plus level instrumentation the client's offer never priced; the whole-plant total remains ~1.1x the client's GBP 1,250,000 offer. [evidence: engine installed-equivalent ~2.4x the client section (v61: GBP 74,465 vs GBP 31,000); whole-plant total 1.11x] · COUNTED: 2× section scope stems (most-specific match) £40,845 · 3× process interconnect (by source endpoint) £2,284 · 1× process interconnect (by destination endpoint) £678 | PASS
C. Fertiliser/fertigation units | 92000 | 41024 | 69741 | -22259 | engine installed-equivalent within 24% of the client section · COUNTED: 2× section scope stems (most-specific match) £40,020 · 1× process interconnect (by source endpoint) £1,004 | PASS
D. Ebb/flow irrigation installation | 895000 | 436757 | 742487 | -152513 | engine installed-equivalent within 17% of the client section · COUNTED: 15× section scope stems (most-specific match) £402,378 · 35× distribution/drain-network pipework £34,379 | PASS
E. Hand watering | 24000 | 11499 | 19548 | -4452 | engine installed-equivalent within 19% of the client section · COUNTED: 3× section scope stems (most-specific match) £11,499 | PASS
F. Process-control computer | 128000 | 121391 | 206365 | 78365 | CONSISTENT WITH RECORDED DECISION — engine 1.6× the client section (installed-equiv £206,365 vs client £128,000). The engine's fuller controls-and-instrumentation design stands versus the leaner client offer — accepted scope, not a defect to tune away. — Tristan Fischer, 2026-07-03. Rationale: The engine includes a SCADA/process-control system plus plant-wide field instrumentation (17 banded level transmitters and the electrical/control cabling) that the client's single process-control-computer line never priced; the whole-plant total remains ~1.1x the client's GBP 1,250,000 offer. [evidence: engine installed-equivalent ~1.8x the client section (v61: GBP 234,124 vs GBP 128,000); whole-plant total 1.11x] · COUNTED: 26× section scope stems (most-specific match) £86,198 · 18× field instrumentation (plant-wide) £33,610 · 26× electrical/control cabling £1,583 | PASS
(engine lines not mapped to any client section) |  | 37387 |  |  | engine-added scope with no client section counterpart (e.g. standby power, skid frames, CIP) — kept VISIBLY unallocated, never forced into a section · COUNTED: 38× no section family match £36,974 · 1× interconnect with no in-scope endpoint £413 | PASS
TOTAL | 1250000 | 808885 | 1375105 | 125105 | engine installed capex (cost stack) vs the client's total offer

## Design basis
Design-basis statement — codes, duties, fluid & utilisation basis |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · arithmetic: min(8, 10 × 26/26 complete rows); content checks: design-basis completeness arithmetic — cell completeness+type contract 104/104 · score = min over checks of… · full audit: Quality & Audit tab
The rules this design was ACTUALLY sized to, one page. Every line is DERIVED LIVE from the module that owns it (pipe/duct sizing constants, the electrical model's BS 7671 ladder, ISO 3098 print legibility, the contract quantities, the Inputs utilisation drivers) with its source stated — never hand-typed. Change the rule at source and this statement follows on rebuild.
Discipline | Item | Value | Unit | Source (module constant / contract quantity — never hand-typed) | Cell check
Process & piping
Process & piping | Pipe sizing basis — target velocity, liquid lines | 1.5 | m/s | connection_sizing.DEFAULT_LIQUID_VELOCITY_MS — D = √(4Q/πv), next standard DN up | PASS
Process & piping | Target velocity, gas / vapour lines | 18 | m/s | connection_sizing.DEFAULT_GAS_VELOCITY_MS | PASS
Process & piping | Target velocity, steam lines | 30 | m/s | connection_sizing.DEFAULT_STEAM_VELOCITY_MS | PASS
Process & piping | Velocity limit, liquid lines (line-list spec) | 3 | m/s | connection_sizing.LIQUID_VELOCITY_LIMIT_MS — the ≤ limit every line is checked against | PASS
Process & piping | Velocity limit, gas lines (erosion) | 30 | m/s | connection_sizing.GAS_VELOCITY_LIMIT_MS (API RP 14E erosion ballpark) | PASS
Process & piping | Velocity limit, steam lines (erosion) | 45 | m/s | connection_sizing.STEAM_VELOCITY_LIMIT_MS | PASS
Process & piping | Standard pipe size ladder | DN15–DN300 (14 standard bores) | DN | connection_sizing.PIPE_DN_LADDER — the ONE ladder the sizer, line list and BoM share | PASS
HVAC
HVAC | Duct sizing basis — target air velocity | 6 | m/s | draw_hvac.DEFAULT_DUCT_VELOCITY_MS — duct area = airflow ÷ target velocity | PASS
HVAC | Duct velocity ceiling (flagged above) | 9 | m/s | draw_hvac.DUCT_VELOCITY_MAX_MS | PASS
Electrical
Electrical | Distribution voltage (this design) | 400 V 3-ph LV |  | electrical_distribution_model.select_distribution_voltage(53 kW) — 53 kW ≤ 250 kW → standard 400 V LV board | PASS
Electrical | Cable conductor sizes — preferred ladder | 1.5–400 (17 sizes) | mm² | electrical_distribution_model.CABLE_CSA_LADDER — BS 7671 / IEC 60228 preferred sizes | PASS
Electrical | Cable ampacity basis | BS 7671 Method C (conservative single-core copper) |  | electrical_distribution_model._CSA_AMPACITY_A | PASS
Electrical | Assumed displacement power factor | 0.95 |  | electrical_distribution_model.POWER_FACTOR (stated, kW↔A) | PASS
Electrical | Practical LV main-board current ceiling | 2500 | A | electrical_distribution_model.PRACTICAL_LV_BOARD_CURRENT_A — past this the model steps up | PASS
Drawings
Drawings | Minimum lettering on printed A1 sheets | 2.5 | mm | a1_print.MIN_TEXT_MM — ISO 3098 minimum lettering height; pagination splits a drawing onto more A1 sheets until met | PASS
Design flows & duties
Design flows & duties | fertigation dosing capacity m3 per hr | 90 | m³/h | orchestratorContract.quantities.fertigation_dosing_capacity_m3_per_hr (calculator) | PASS
Design flows & duties | fertigation dosing total m3 h | 90 | m3/h | orchestratorContract.quantities.fertigation_dosing_total_m3_h (demand-coverage) | PASS
Design flows & duties | irrigation demand m3 h | 90 | m³/h | orchestratorContract.quantities.irrigation_demand_m3_h (calculator) | PASS
Design flows & duties | irrigation pump flow m3 h | 90 | m3/h | orchestratorContract.quantities.irrigation_pump_flow_m3_h (tool:irrigation:pump-sizing) | PASS
Design flows & duties | uv disinfection throughput m3 h | 90 | m³/h | orchestratorContract.quantities.uv_disinfection_throughput_m3_h (calculator) | PASS
Design flows & duties | transformer kva | 75 | kVA | orchestratorContract.quantities.transformer_kva (tool:electrical:transformer-sizing) | PASS
Design flows & duties | connected electrical load kw | 53 | kW | orchestratorContract.quantities.connected_electrical_load_kw (calculator) | PASS
Process fluid
Process fluid | Design fluid density | 1000 | kg/m³ | process-fluid density (median of 3 engine worked-calc input(s)) — resolved by _process_fluid_density from the engine's own worked-calc inputs | PASS
Utilisation drivers
Utilisation drivers | Water / service utilisation (levelised-cost divisor) | 0.25 |  | LIVE ← 'Inputs & Assumptions'!$B$14 — annual delivered volume = design flow × 8760 × THIS driver | PASS
Utilisation drivers | Electrical load factor (energy line only) | 0.65 |  | LIVE ← 'Inputs & Assumptions'!$B$11 — average÷peak electrical ratio — sizes the energy cost, never the water divisor | PASS
Utilisation drivers | Operating hours basis | 8000 | h/yr | LIVE ← 'Inputs & Assumptions'!$B$12 — hours per year the plant runs | PASS

## Drawings
Drawing register | [8 empty] | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · drawing-register integrity: every registered A1 print PDF exists on disk + ISO 3098 2.5 mm lettering bar — registered drawings with their print set present 4/5; register… · full audit: Quality & Audit tab
Every engineering drawing and render in this dossier. The File column names the print-ready ISO A1 vector PDF set in the run's drawings/ folder (841 × 594 mm, smallest lettering ≥ 2.5 mm on paper per ISO 3098; multi-sheet drawings carry match lines). The workbook tabs embed reduced PNG previews — print from the A1 PDFs, never from the previews.
Drawing No. | Title | Rev | Scale | Sheets | Min lettering | File (A1 print set) | Preview tab | File check | Audit: PDFs found | Audit: missing sheets | Cell check
FF-GA-001 | General Arrangement | P1 | 1:200 (@ A1) | 1 | 3 mm | drawings/ga-A1.pdf | GA — General Arrangement | ✓ 1 sheet PDF(s) on disk | 1 |  | PASS
FF-PID-001 | Piping & Instrumentation Diagram | P1 | NTS | 12 | 3.25 mm | drawings/pid-A1.pdf drawings/pid-A1-sheet2.pdf drawings/pid-A1-sheet3.pdf drawings/pid-A1-sheet4.pdf drawings/pid-A1-sheet5.pdf drawings/pid-A1-sheet6.pdf drawings/pid-A1-sheet7.pdf drawings/pid-A1-sheet8.pdf drawings/pid-A1-sheet9.pdf drawings/pid-A1-sheet10.pdf drawings/pid-A1-sheet11.pdf drawings/pid-A1-sheet12.pdf | P&ID | ✓ 12 sheet PDF(s) on disk | 12 |  | PASS
FF-BFD-001 | Block Flow Diagram | P1 | NTS | 6 | 2.7 mm | drawings/bfd-A1.pdf drawings/bfd-A1-sheet2.pdf drawings/bfd-A1-sheet3.pdf drawings/bfd-A1-sheet4.pdf drawings/bfd-A1-sheet5.pdf drawings/bfd-A1-sheet6.pdf | BFD — Block Flow | ✓ 6 sheet PDF(s) on disk | 6 |  | PASS
FF-SLD-001 | Single-Line Electrical Diagram | P1 | NTS | 1 | 2.79 mm | drawings/single-line-A1.pdf | Electrical | ✓ 1 sheet PDF(s) on disk | 1 |  | PASS
FF-HVAC-001 | HVAC / Ventilation Layout | P1 | 1:500 (@ A1) | — | — | — no A1 print set (PNG/SVG embedded only) | HVAC | — | 0 |  | ⚠ FAIL — 'File check' placeholder '—'
Photoreal renders — 8 view(s) from the Blender scene build (drawing-manifest renders[])
# | Render | File | Caption |  |  |  | Preview tab |  | Cell check
1 | Render 1 — Interior iso | 00-hero.png | Interior render — three-quarter hero perspective · plant envelope 22.1 × 24.4 × 4.5 m · principal equipment: TK-106 Drain Water Tank · TK-107 Drain Water Tank · TK-108 Fresh Water Tank · Z-101 Reverse Osmosis Skid · Z-102 Uf Module Bank |  |  |  | Renders |  | PASS
2 | Render 2 — Interior plan | 01-top.png | Interior render — plan view, looking down · plant envelope 22.1 × 24.4 × 4.5 m · principal equipment: TK-106 Drain Water Tank · TK-107 Drain Water Tank · TK-108 Fresh Water Tank · Z-101 Reverse Osmosis Skid · Z-102 Uf Module Bank |  |  |  | Renders |  | PASS
3 | Render 3 — Interior FR iso | 02-corner-FR.png | Interior render — front-right corner perspective · plant envelope 22.1 × 24.4 × 4.5 m · principal equipment: TK-106 Drain Water Tank · TK-107 Drain Water Tank · TK-108 Fresh Water Tank · Z-101 Reverse Osmosis Skid · Z-102 Uf Module Bank |  |  |  | — |  | PASS
4 | Render 4 — Interior BL iso | 03-corner-BL.png | Interior render — back-left corner perspective · plant envelope 22.1 × 24.4 × 4.5 m · principal equipment: TK-106 Drain Water Tank · TK-107 Drain Water Tank · TK-108 Fresh Water Tank · Z-101 Reverse Osmosis Skid · Z-102 Uf Module Bank |  |  |  | — |  | PASS
5 | Render 5 — Exterior iso | exterior/00-hero.png | Exterior render — three-quarter hero perspective · plant envelope 22.1 × 24.4 × 4.5 m · building shell + site apron (equipment enclosed) |  |  |  | Renders |  | PASS
6 | Render 6 — Exterior plan | exterior/01-top.png | Exterior render — plan view, looking down · plant envelope 22.1 × 24.4 × 4.5 m · building shell + site apron (equipment enclosed) |  |  |  | — |  | PASS
7 | Render 7 — Exterior FR iso | exterior/02-corner-FR.png | Exterior render — front-right corner perspective · plant envelope 22.1 × 24.4 × 4.5 m · building shell + site apron (equipment enclosed) |  |  |  | Renders |  | PASS
8 | Render 8 — Exterior BL iso | exterior/03-corner-BL.png | Exterior render — back-left corner perspective · plant envelope 22.1 × 24.4 × 4.5 m · building shell + site apron (equipment enclosed) |  |  |  | — |  | PASS

## BFD — Block Flow
BFD — Block Flow | ↑ Contents
⬤ TAB QUALITY 8.9/10 · PASS (target ≥8, live from the Quality & Audit score cell) · block-flow part-coverage arithmetic (parts_ledger) — drawing part coverage (block-flow-diagram) 16/18 · score = min over checks of 10 × passed/checked · full audit: Quality & Audit tab
Block flow diagram of the process.
Full-size vector sheets: drawings/bfd-A1.pdf (sheets 1-6, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: each block is one major process step — follow the stream arrows left to right; block names match the Quantities and BoM module groupings.

## P&ID
P&ID | ↑ Contents
⬤ TAB QUALITY 9/10 · PASS (target ≥8, live from the Quality & Audit score cell) · P&ID part-coverage arithmetic (parts_ledger ✓/✗ vs the BoM) — drawing part coverage (pid) 38/42 · score = min over checks of 10 × passed/checked · full audit: Quality & Audit tab
Piping & instrumentation diagram.
Full-size vector sheets: drawings/pid-A1.pdf (sheets 1-12, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: top band = the process train in flow order (follow the numbered lines left to right), lower band = utility / dosing tie-ins; line numbers match the Process schedules tab.

## Process schedules
Process schedules | [8 empty] | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · schedule column contract (per-cell completeness + type over every schedule row, from the drawings/*.md source) — cell completeness+type contract 369/454 · score = min ov… · full audit: Quality & Audit tab
Valve list and instrument index — sortable sections parsed from process-schedules.md and cross-referenced to the P&ID. The LINE LIST lives once, on the 'Line & velocity' tab.
Process line list — see the 'Line & velocity' tab
→ Line & velocity | THE line list: every routed line ONCE (as-routed tags, e.g. 201-PR-DN65) with its size, computed flow/velocity vs the erosion band, length, £ and per-row contract check. The 81-row block previously duplicated here carried the same physical lines in two tag dialects, plus artefact rows (a from==to self-loop; 4-20 mA instrument signal cables misfiled as pipes) — signals are on the instrument index below, never the pipe list.
Process valve list
Tag | Type | Service | Line / location | Size | Set / Cv | Fail | P&ID | Cell check
NV-201 | Non-return (check) | Check Valve | 201-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
PCV-201 | Control valve | Flow Control Valve (assembly component) | 242-WT-DN20 | DN20 | modulating | FC | FF-PID-001 S1-S12 | PASS
PSV-201 (×2) | Pressure relief (PSV) | Tank Vent / Pressure Relief (assembly component) | V-106 | line size | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Set / Cv' placeholder '—'; 'Fail' placeholder '—'
HV-201 (×2) | Manual isolation | Suction Isolation Valve (assembly component) | 202-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
HV-202 (×2) | Manual isolation | Discharge Isolation Valve (assembly component) | 203-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
NV-202 (×2) | Non-return (check) | Non-Return Valve (assembly component) | 204-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
HV-203 | Manual isolation | Suction Isolation Valve (assembly component) | 205-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
HV-204 | Manual isolation | Discharge Isolation Valve (assembly component) | 206-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
NV-203 | Non-return (check) | Non-Return Valve (assembly component) | 207-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
HV-205 (×2) | Manual isolation | Suction Isolation Valve (assembly component) | 242-WT-DN20 | DN20 | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Set / Cv' placeholder '—'; 'Fail' placeholder '—'
HV-206 (×2) | Manual isolation | Discharge Isolation Valve (assembly component) | 242-WT-DN20 | DN20 | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Set / Cv' placeholder '—'; 'Fail' placeholder '—'
NV-204 (×2) | Non-return (check) | Non-Return Valve (assembly component) | 242-WT-DN20 | DN20 | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Set / Cv' placeholder '—'; 'Fail' placeholder '—'
HV-207 | Manual isolation | Suction Isolation Valve (assembly component) | 208-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
HV-208 | Manual isolation | Discharge Isolation Valve (assembly component) | 209-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
NV-205 | Non-return (check) | Non-Return Valve (assembly component) | 210-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
HV-209 | Manual isolation | Suction Isolation Valve (assembly component) | 211-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
HV-210 | Manual isolation | Discharge Isolation Valve (assembly component) | 212-WT | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
NV-206 | Non-return (check) | Non-Return Valve (assembly component) | 213-WT | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
XV-201 | Solenoid shut-off | Solenoid Valve | 214-PR | — | on/off (tight-shutoff) | FC | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'
XV-202 (×200) | Actuated isolation | Pneumatic Actuated Valves | 215-PR | — | on/off (tight-shutoff) | FC | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'
HV-211 | Manual isolation | Manual Isolation Valves | 216-WT | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
XV-203 (×200) | Actuated isolation | Pneumatic Actuators | 217-WT | — | on/off (tight-shutoff) | FC | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'
PCV-202 | Control valve | Flow Control Valves | 242-WT-DN20 | DN20 | modulating | FC | FF-PID-001 S1-S12 | PASS
FCV-201–202 | Control valve | DN100 modulating control valve (45 m³/h @ 2 m/s), on the inlet of Softener Vessel; modulated against the tank level transmitter to balance the recirculation flow | 242-WT-DN20 | DN20 | modulating | FC | FF-PID-001 S1-S12 | PASS
XV-204 | Solenoid shut-off | Solenoid Valve | 218-PR | — | on/off (tight-shutoff) | FC | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'
HV-212 | Manual isolation | Manual Ball Valve | 219-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
PCV-203 | Control valve | Pneumatic Control Valve | 220-WT | — | modulating | FC | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'
HV-213 | Manual isolation | Manual Ball Valve | 221-WT | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
XV-205 | Actuated isolation | Automated Ball Valves | 222-PR | — | on/off (tight-shutoff) | FC | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'
PSV-202 | Pressure relief (PSV) | Pressure Relief Valve | V-106 | line size | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Set / Cv' placeholder '—'; 'Fail' placeholder '—'
NV-207 | Non-return (check) | Check Valve | 223-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
HV-214 | Manual isolation | Isolation Valves | 224-PR | — | — | — | FF-PID-001 S1-S12 | ⚠ FAIL — 'Size' placeholder '—'; 'Set / Cv' placeholder '—' +1 more
Process instruments
Tag | ISA | Service | Measured | Type | Location | Range | Signal | Loop | Cell check
PT-218 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | X-912 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-219 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | Z-102 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-220…224 | PT | Discharge Pressure Gauge — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 (4 off) | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-222 | PT | Discharge Pressure Gauge — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-225 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | V-105 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-226 | PT | Discharge Pressure Gauge — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-227 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-228 | PT | Discharge Pressure Gauge — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-229 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | P-101 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-230 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | X-912 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-231 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | X-913 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
FT-201 | FT | Flow Meter | Flow | Electromagnetic | lines (e.g. 243-PR-DN32) | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
AT-202 | AT (pH) | Ph Sensor | pH / conductivity | Memosens electrode | vessels (e.g. V-106) | 0–14 pH | 4–20 mA | FF-PID-001 S1-S12 | PASS
AT-203 | AT (ORP) | Orp Sensor | Redox (ORP) | Pt ORP electrode | vessels (e.g. V-106) | −1500 to +1500 mV | 4–20 mA | FF-PID-001 S1-S12 | PASS
LT-201…213 | LT | Level Transmitter | Level | Guided-radar | vessels (e.g. V-106) (13 off) | 0–1.4 m | 4–20 mA | FF-PID-001 S1-S12 | PASS
LT-214 | LT | Level Transmitter | Level | Guided-radar | Z-101 | 0–3 m | 4–20 mA | FF-PID-001 S1-S12 | PASS
LT-215…217 | LT | Level Transmitter | Level | Guided-radar | vessels (e.g. V-106) (3 off) | 0–4 m | 4–20 mA | FF-PID-001 S1-S12 | PASS
AT-201 | AT (pH) | pH Analyser | pH / conductivity | ISE / glass electrode | TK-114 | 0–14 pH | 4–20 mA | FF-PID-001 S1-S12 | PASS
PT-201…217 | PT | Pressure Transmitter | Pressure | Piezoresistive | P-101 (17 off) | 0–5 bar | 4–20 mA | FF-PID-001 S1-S12 | PASS
AT-204 | AT | Silica Analyzer | Composition | NDIR analyser | vessels (e.g. V-106) | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
FT-202 | FT | Flow Meter | Flow | Electromagnetic | lines (e.g. 243-PR-DN32) | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'
PT-232 | PT | Differential-Pressure Gauges — TBD (detailed design) | Pressure | Coplanar gauge / DP | X-912 | — | 4–20 mA | FF-PID-001 S1-S12 | ⚠ FAIL — 'Range' placeholder '—'

## GA — General Arrangement
GA — General Arrangement | ↑ Contents
⬤ TAB QUALITY 9.7/10 · PASS (target ≥8, live from the Quality & Audit score cell) · GA mechanism: parts-ledger coverage × default-size litter × layout-divergence × typed-shape checks — drawing part coverage (general-arrangement) 29/30 · score = min over… · full audit: Quality & Audit tab
General arrangement / plant layout.
Full-size vector sheets: drawings/ga-A1.pdf (sheet 1 of 1, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: plan view with elevations — equipment outlines carry the same tags as the Part names tab; dimensions in mm, datum ±0.000 = finished floor level.

## HVAC
HVAC | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · HVAC duty-scoped check: contract duty signal → drawing coverage; no duty → honest out-of-scope disclosure (capped 8) · full audit: Quality & Audit tab
HVAC / ventilation layout.
Full-size vector sheets: none for this drawing (PNG/SVG master only) — see the Drawings register tab. Reading guide: duct runs overlay the GA footprint with supply vs extract airflow arrows; equipment tags match the Part names tab.

## Electrical
Electrical — single-line diagram + panel / load schedule | [10 empty] | ↑ Contents
⬤ TAB QUALITY 9.6/10 · PASS (target ≥8, live from the Quality & Audit score cell) · column-contract arithmetic: 10 × 22/23 rows passing; content checks: panel-schedule column contract + single-line drawing coverage — cell completeness+type contract 187/… · full audit: Quality & Audit tab
The electrical design on ONE tab: single-line diagram (preview) above, the panel / load schedule below. Every number on this tab renders from ONE dataset — the schedule (the converged connection schedule): Design I = P·1000 / (√3·V·pf·η) — pf 0.85 / η 0.90 for motor circuits, pf 1.0 / η 1.0 for resistive loads — from each circuit's INSTALLED motor frame. ΔU % is the cable volt-drop over its length / CSA at Design I. 'In spec' is a LIVE formula = (ΔU ≤ 5 %) — a missing/dash ΔU renders ✗, never a pass. Auto-generated; not for construction. ROW CHECK CONTRACT (score = 10 × rows-passing ÷ rows = 10 × 22/23 = 9.6): Ckt/Description=required_nonempty · Conn. load (kW)=required_nonempty · Design I (A)=computed · Protective device=computed · Cable=computed · Length (m)=required_nonempty · ΔU (%)=computed · In spec=computed · Board reconciliation=computed · Drawing ↔ schedule=computed. A dash / empty / unverifiable contracted cell FAILS its row — honest red beats fake green.
Full-size vector sheets: drawings/single-line-A1.pdf (sheet 1 of 1, ISO A1, lettering ≥2.5 mm) — see the Drawings register tab. Reading guide: read top-down from the utility incomer through the main board to each feeder; feeder tags and loads match the Panel schedule tab.
Convention: the schedule below is the single source for the electrical numbers on this tab. On the drawing, a ×N grouped circuit is labelled with its PER-UNIT current (the schedule's Design I is the whole circuit), and the LV system is stated at its 400 V nominal (a legacy '415 V' label names the same UK LV system). Where a drawing label and the schedule differ, the schedule governs.
⛔ 1 of 23 rows FAIL — single cause: board reference(s) absent from the single-line drawing: MAIN DISTRIBUTION BOARD (TP&N)
Fix route: route the electrical circuits in the scene (wire the electrical_bus edges) so route-manifest / connection-schedule carry real cable lengths, compute ΔU% = f(length, CSA, Design I) in draw_panel_schedule at source, and generate the single-line + schedule from the ONE distribution dataset so kVA / voltage / board names cannot diverge
MAIN DISTRIBUTION BOARD (TP&N)
Field | Value | Cell check
Board reference | Motor Control Center | PASS
Board type | Main distribution board | PASS
Supply source | Utility LV incomer (400 V distribution board) | PASS
System | 400 V 3-phase + N (TP&N) | PASS
Busbar rating | 100 A | PASS
Incoming feeder | 1.5 mm² · 20.0 m · ΔU 0.142% | PASS
Total connected load | 45.2 kW
Board demand (busbar) | 87 A | PASS
MAIN DISTRIBUTION BOARD (TP&N)
Ckt | Description | Ways | Conn. load (kW) | Design I (A) | Protective device | Cable (CSA · cores) | Length (m) | ΔU (%) | In spec | Row check | Audit: device rating (A) | Audit: Iz (A) — BS 7671 Method-C ampacity | Audit: check evidence (build-computed) | Audit: kW (parsed per-unit) | Audit: Design I (parsed) | Cell check
W1 | 3 Phase Power Input | 1 | 0.6 | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 5.7 | 0.041 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W2 | Piping Network | 1 | 0.5 | 0.9 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 25.8 | 0.151 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W3 | Uv Disinfection | 1 | 4 | 7.5 | 10 A MCB (sized) | 1.5 mm² · 3c+E | 24.9 | 1.212 | ✓ | PASS | 10 | 20 |  |  |  | PASS
W4–5 | Fertigation Dosing Pump | 2 | 7.50 (×2=15.0) | 15.1 | 16 A MCB (sized) | 1.5 mm² · 3c+E | 23.7 | 2.328 | ✓ | PASS | 16 | 20 |  | 7.5 |  | PASS
W6 | Hand Watering Pump | 1 | 2.8 | 5.3 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 31.2 | 1.076 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W7–8 | Drain Transfer Pump | 2 | 1.92 (×2=3.8) | 3.8 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 27.3 | 0.675 | ✓ | PASS | 6 | 20 |  | 1.92 |  | PASS
W9–10 | Cloth Filter | 2 | 0.60 (×2=1.2) | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 21.2 | 0.152 | ✓ | PASS | 6 | 20 |  | 0.6 |  | PASS
W11 | Irrigation / nutrient pump | 1 | 9.65 | 18.2 | 20 A MCB (sized) | 1.5 mm² · 3c+E | 28.1 | 3.316 | ✓ | PASS | 20 | 20 |  |  |  | PASS
W12 | Ro High Pressure Pump | 1 | 4.2 | 7.9 | 10 A MCB (sized) | 1.5 mm² · 3c+E | 32.4 | 1.664 | ✓ | PASS | 10 | 20 |  |  |  | PASS
W13 | Gac Filter | 1 | 0.6 | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 33.7 | 0.241 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W14 | Permeate Outlet | 1 | 0.6 | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 10.5 | 0.075 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W15 | Concentrate Outlet | 1 | 0.6 | 1.1 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 7.5 | 0.054 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W16 | Electrical Control Panel | 1 | 0.2 | 0.4 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 3.6 | 0.009 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W17 | Control + Instrument UPS | 1 | 0.5 | 0.9 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 3.6 | 0.021 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W18 | SCADA / Plant Control System | 1 | 0.5 | 0.9 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 3.3 | 0.019 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W19 | Electrical Control Cabinet | 1 | 0.2 | 0.4 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 28 | 0.073 | ✓ | PASS | 6 | 20 |  |  |  | PASS
W20 | Digital Control Panel (control / aux feeder) | 1 | 0.2 | 0.4 | 6 A MCB (sized) | 1.5 mm² · 3c+E | 3.8 | 0.01 | ✓ | PASS | 6 | 20 |  |  |  | PASS
| TOTALS |  | 45.2 kW | 87 A
Main Switchboard
Field | Value | Cell check
Board reference | Main Switchboard | PASS
Board type | Sub-distribution board | PASS
Supply source | Local sub-distribution (MV feeder → local step-down transformer) | PASS
System | 400 V 3-phase + N (TP&N) | PASS
Busbar rating | 20 A | PASS
Incoming feeder | 1.5 mm² · 5.9 m · ΔU 0.042% | PASS
Total connected load | 9.7 kW
Board demand (busbar) | 18 A | PASS
Main Switchboard
Ckt | Description | Ways | Conn. load (kW) | Design I (A) | Protective device | Cable (CSA · cores) | Length (m) | ΔU (%) | In spec | Row check | Audit: device rating (A) | Audit: Iz (A) — BS 7671 Method-C ampacity | Audit: check evidence (build-computed) | Audit: kW (parsed per-unit) | Audit: Design I (parsed) | Cell check
W1 | Motor Control Center | 1 | 9.7 | 18.3 | 20 A MCB (sized) | 1.5 mm² · 3c+E | 20 | 2.377 | ✓ | PASS | 20 | 20 |  |  |  | PASS
| TOTALS |  | 9.7 kW | 18 A
Board & drawing reconciliation — contract checks (scored with the circuit rows above). These compare TWO ARTEFACTS (schedule ↔ single-line drawing ↔ contract): each side's value is EMBEDDED on the 'Audit data' sheet with its provenance, and the Row check is a live formula over those operand cells.
Check | Measured / compared | [7 empty] | Row check |  | Cell check
MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] | Σ circuit design current 87 A vs busbar demand 87 A (ratio 1); busbar rating: 100 A | [7 empty] | PASS |  | PASS
Main Switchboard · [board reconciliation] | Σ circuit design current 18 A vs busbar demand 18 A (ratio 1); busbar rating: 20 A | [7 empty] | PASS |  | PASS
single-line ↔ schedule · system voltage | schedule system 400 V 3-phase; drawing voltages: 11000/400 V, 400 V | [7 empty] | PASS |  | PASS
single-line ↔ schedule · board hierarchy | schedule boards: MAIN DISTRIBUTION BOARD (TP&N), Main Switchboard | [7 empty] | FAIL — board reference(s) absent from the single-line drawing: MAIN DISTRIBUTION BOARD (TP&N) |  | PASS
single-line ↔ schedule · transformer kVA | drawing transformer 75.0 kVA vs contract quantity 75.0 kVA | [7 empty] | PASS |  | PASS

## Line & velocity
Line & velocity schedule | [11 empty] | ↑ Contents
⬤ TAB QUALITY 9.6/10 · PASS (target ≥8, live from the Quality & Audit score cell) · column-contract arithmetic: 10 × 71/74 rows passing; content checks: line & velocity column contract (per-row Row check) — cell completeness+type contract 518/518 · scor… · full audit: Quality & Audit tab
Every sized run, SPLIT so units never mix: process-pipe lines (flow, velocity vs the erosion band) · electrical & signal cables (current A, volt-drop band) · other services. Velocity is COMPUTED (the sizer's as-sized value when it carried a real flow, else v = Q ÷ A from the endpoint-matched contract flow over the sizer's DN bore); 'In spec' is the computed band comparison — never a default tick. Basis shows the flow/velocity derivation + how each Line £ is built. ROW CHECK CONTRACT (score = 10 × rows-passing ÷ rows = 10 × 71/74 = 9.6): Tag/From/To/Size=required_nonempty · Rating=computed · Velocity / ΔU=computed · Spec limit=required_nonempty · In spec=computed · Length (m)=required_nonempty · Line £ + Basis=required_nonempty. A dash / empty / unverifiable contracted cell FAILS its row — honest red beats fake green.
⛔ 3 of 74 rows FAIL — top causes: 2× velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint; 1× no carried current on the run; ΔU% missing — volt-drop unverifiable (dash is never in-spec)
Fix route: author the real flow demand (required_value) on every fluid topology edge at source (universal-contract-sizing → connection ledger) so connection_sizing sizes bores from true flows; the schedule then carries computed velocities and the band check passes on the re-sized lines
Process pipe lines — flow (m³/s) · velocity limit ≤ 3 m/s
Basis note — common to the rows below (factored out of the per-row cells): cost model: model:uk-2026-supply+install
Tag | From | To | Size | Rating | Velocity / ΔU | Spec limit | Length (m) | In spec | Line £ | Basis | Row check | Audit: band | Audit: check evidence (build-computed) | Cell check
201-PR-DN65 | Gac Softener | Softener Vessel | DN65 | 14.5 m3/h | 1.304 | ≤3 m/s velocity | 10.79 | ✓ | 757.4 | DN65 pipe, 10.8 m, ΔP≈2.9 kPa · £60/m × 10.8 m · install £647 · as-sized by connection_sizing (post-upsize) from 14.5 m3/h | PASS | 3 |  | PASS
202-PR-DN125 | Gac Softener | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 20.37 | ✓ | 2908.1 | DN125 pipe, 20.4 m, ΔP≈1.3 kPa · £130/m × 20.4 m · install £2,648 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
203-PR-DN50 | Uf Module Bank | Ro High Pressure Pump | DN50 | 11 m3/h | 1.412 | ≤3 m/s velocity | 21.53 | ✓ | 1117.44 | DN50 pipe, 21.5 m, ΔP≈8.3 kPa · £48/m × 21.5 m · install £1,033 · as-sized by connection_sizing (post-upsize) from 11 m3/h | PASS | 3 |  | PASS
204-PR-DN125 | Uf Module Bank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 22.14 | ✓ | 3138.2 | DN125 pipe, 22.1 m, ΔP≈1.4 kPa · £130/m × 22.1 m · install £2,878 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
205-PR-DN50 | Ro High Pressure Pump | Reverse Osmosis Skid | DN50 | 11 m3/h | 1.412 | ≤3 m/s velocity | 30.89 | ✓ | 1566.72 | DN50 pipe, 30.9 m, ΔP≈12.0 kPa · £48/m × 30.9 m · install £1,483 · as-sized by connection_sizing (post-upsize) from 11 m3/h | PASS | 3 |  | PASS
206-PR-DN125 | Ro High Pressure Pump | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 35.13 | ✓ | 4826.9 | DN125 pipe, 35.1 m, ΔP≈2.3 kPa · £130/m × 35.1 m · install £4,567 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
207-PR-DN150 | Cloth Filter | Gac Filter | DN150 | 80 m3/h | 1.191 | ≤3 m/s velocity | 18.58 | ✓ | 3405.7 | DN150 pipe, 18.6 m, ΔP≈1.4 kPa · £165/m × 18.6 m · install £3,066 · as-sized by connection_sizing (post-upsize) from 80 m3/h | PASS | 3 |  | PASS
208-PR-DN125 | Cloth Filter | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 23.46 | ✓ | 3309.8 | DN125 pipe, 23.5 m, ΔP≈1.5 kPa · £130/m × 23.5 m · install £3,050 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
209-PR-DN150 | Gac Filter | Uv Disinfection | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 20.69 | ✓ | 3753.85 | DN150 pipe, 20.7 m, ΔP≈2.0 kPa · £165/m × 20.7 m · install £3,414 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
210-PR-DN125 | Gac Filter | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 29.59 | ✓ | 4106.7 | DN125 pipe, 29.6 m, ΔP≈1.9 kPa · £130/m × 29.6 m · install £3,847 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
211-PR-DN125 | Uv Disinfection | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 27.71 | ✓ | 3862.3 | DN125 pipe, 27.7 m, ΔP≈1.8 kPa · £130/m × 27.7 m · install £3,602 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
212-WT-DN125 | Drain Collection Sump | Drain Water Tank | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 11.74 | ✓ | 1786.2 | DN125 pipe, 11.7 m, ΔP≈0.8 kPa · £130/m × 11.7 m · install £1,526 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
213-PR-DN150 | Drain Collection Sump | Uv Disinfection | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 22.39 | ✓ | 4034.35 | DN150 pipe, 22.4 m, ΔP≈2.1 kPa · £165/m × 22.4 m · install £3,694 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
214-PR-DN65 | Drain Collection Sump | Softener Vessel | DN65 | 14.5 m3/h | 1.304 | ≤3 m/s velocity | 8.95 | ✓ | 647 | DN65 pipe, 9.0 m, ΔP≈2.4 kPa · £60/m × 8.9 m · install £537 · as-sized by connection_sizing (post-upsize) from 14.5 m3/h | PASS | 3 |  | PASS
215-WT-DN80 | Drain Collection Sump | Hand Watering Pump | DN80 | 25 m3/h | 1.457 | ≤3 m/s velocity | 29.38 | ✓ | 2314.12 | DN80 pipe, 29.4 m, ΔP≈7.4 kPa · £74/m × 29.4 m · install £2,174 · as-sized by connection_sizing (post-upsize) from 25 m3/h | PASS | 3 |  | PASS
216-PR-DN150 | Drain Collection Sump | Cloth Filter | DN150 | 80 m3/h | 1.191 | ≤3 m/s velocity | 19.46 | ✓ | 3550.9 | DN150 pipe, 19.5 m, ΔP≈1.5 kPa · £165/m × 19.5 m · install £3,211 · as-sized by connection_sizing (post-upsize) from 80 m3/h | PASS | 3 |  | PASS
217-PR-DN65 | Drain Collection Sump | Gac Softener | DN65 | 14.5 m3/h | 1.304 | ≤3 m/s velocity | 9.38 | ✓ | 672.8 | DN65 pipe, 9.4 m, ΔP≈2.5 kPa · £60/m × 9.4 m · install £563 · as-sized by connection_sizing (post-upsize) from 14.5 m3/h | PASS | 3 |  | PASS
218-PR-DN150 | Drain Collection Sump | Irrigation Pump | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 26.68 | ✓ | 4742.2 | DN150 pipe, 26.7 m, ΔP≈2.5 kPa · £165/m × 26.7 m · install £4,402 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
219-PR-DN125 | Drain Collection Sump | Reverse Osmosis Skid | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 3.73 | ✓ | 744.9 | DN125 pipe, 3.7 m, ΔP≈0.2 kPa · £130/m × 3.7 m · install £485 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
220-PR-DN50 | Drain Collection Sump | Ro High Pressure Pump | DN50 | 11 m3/h | 1.412 | ≤3 m/s velocity | 30.42 | ✓ | 1544.16 | DN50 pipe, 30.4 m, ΔP≈11.8 kPa · £48/m × 30.4 m · install £1,460 · as-sized by connection_sizing (post-upsize) from 11 m3/h | PASS | 3 |  | PASS
221-PR-DN125 | Drain Collection Sump | Gac Filter | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 23.98 | ✓ | 3377.4 | DN125 pipe, 24.0 m, ΔP≈1.6 kPa · £130/m × 24.0 m · install £3,117 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
222-PR-DN125 | Drain Collection Sump | Uf Module Bank | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 8.59 | ✓ | 1376.7 | DN125 pipe, 8.6 m, ΔP≈0.6 kPa · £130/m × 8.6 m · install £1,117 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
223-PR-DN32 | Drain Collection Sump | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 20.31 | ✓ | 742.54 | DN32 pipe, 20.3 m, ΔP≈8.9 kPa · £34/m × 20.3 m · install £691 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
224-PR-DN32 | Drain Collection Sump | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 23.93 | ✓ | 865.62 | DN32 pipe, 23.9 m, ΔP≈10.5 kPa · £34/m × 23.9 m · install £814 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
225-WT-DN125 | Drain Water Tank | Drain Transfer Pump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 27.54 | ✓ | 3840.2 | DN125 pipe, 27.5 m, ΔP≈1.8 kPa · £130/m × 27.5 m · install £3,580 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
226-PR-DN32 | Drain Transfer Pump | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 27.53 | ✓ | 988.02 | DN32 pipe, 27.5 m, ΔP≈12.0 kPa · £34/m × 27.5 m · install £936 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
227-PR-DN32 | Cip Tank | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 3.33 | ✓ | 165.22 | DN32 pipe, 3.3 m, ΔP≈1.5 kPa · £34/m × 3.3 m · install £113 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
228-PR-DN125 | Cip Tank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 20.64 | ✓ | 2943.2 | DN125 pipe, 20.6 m, ΔP≈1.3 kPa · £130/m × 20.6 m · install £2,683 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
229-WT-DN32 | Cip Tank | Fresh Water Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 13.88 | ✓ | 523.92 | DN32 pipe, 13.9 m, ΔP≈6.1 kPa · £34/m × 13.9 m · install £472 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
230-PR-DN125 | Cip Tank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 24.48 | ✓ | 3442.4 | DN125 pipe, 24.5 m, ΔP≈1.6 kPa · £130/m × 24.5 m · install £3,182 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
231-WT-DN25 | Fresh Water Tank | Nutrient Tank | DN25 (nominal — flow unknown) | — | UNVERIFIED | ≤3 m/s velocity (UNVERIFIED — no flow demand) | 3.9 | ✗ | 149.2 | DN25 nominal pipe, 3.9 m (flow unknown) · £28/m × 3.9 m · install £109 | FAIL — velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint |  | velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint | PASS
232-WT-DN150 | Fresh Water Tank | Permeate Outlet | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 24.74 | ✓ | 2653.26 | DN150 pipe, 24.7 m, ΔP≈2.3 kPa · £99/m × 24.7 m · install £2,449 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
233-WT-DN125 | Fresh Water Tank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 27.23 | ✓ | 3799.9 | DN125 pipe, 27.2 m, ΔP≈1.8 kPa · £130/m × 27.2 m · install £3,540 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
234-WT-DN125 | Fresh Water Tank | Drain Transfer Pump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 36.54 | ✓ | 5010.2 | DN125 pipe, 36.5 m, ΔP≈2.4 kPa · £130/m × 36.5 m · install £4,750 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
235-WT-DN25 | Fresh Water Tank | Drain Water Tank | DN25 (nominal — flow unknown) | — | UNVERIFIED | ≤3 m/s velocity (UNVERIFIED — no flow demand) | 19.98 | ✗ | 599.44 | DN25 nominal pipe, 20.0 m (flow unknown) · £28/m × 20.0 m · install £559 | FAIL — velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint |  | velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint | PASS
236-WT-DN80 | Fertigation Dosing Pump | Hand Watering Pump | DN80 | 25 m3/h | 1.457 | ≤3 m/s velocity | 29.63 | ✓ | 2332.62 | DN80 pipe, 29.6 m, ΔP≈7.5 kPa · £74/m × 29.6 m · install £2,193 · as-sized by connection_sizing (post-upsize) from 25 m3/h | PASS | 3 |  | PASS
237-PR-DN125 | Fertigation Dosing Pump | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 19.37 | ✓ | 2778.1 | DN125 pipe, 19.4 m, ΔP≈1.3 kPa · £130/m × 19.4 m · install £2,518 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
238-WT-DN150 | Hand Watering Pump | Irrigation Pump | DN150 | 90 m3/h | 1.34 | ≤3 m/s velocity | 6.54 | ✓ | 1419.1 | DN150 pipe, 6.5 m, ΔP≈0.6 kPa · £165/m × 6.5 m · install £1,079 · as-sized by connection_sizing (post-upsize) from 90 m3/h | PASS | 3 |  | PASS
239-WT-DN125 | Hand Watering Pump | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 33.5 | ✓ | 4615 | DN125 pipe, 33.5 m, ΔP≈2.2 kPa · £130/m × 33.5 m · install £4,355 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
240-PR-DN125 | Irrigation Pump | Distribution Manifold | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 1.87 | ✓ | 503.1 | DN125 pipe, 1.9 m, ΔP≈0.1 kPa · £130/m × 1.9 m · install £243 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
241-PR-DN125 | Irrigation Pump | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 31.06 | ✓ | 4297.8 | DN125 pipe, 31.1 m, ΔP≈2.0 kPa · £130/m × 31.1 m · install £4,038 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
242-WT-DN20 | Ultrafiltration Module | Fresh Water Tank | DN20 | 1.35 m3/h | 1.083 | ≤3 m/s velocity | 20.6 | ✓ | 291.12 | DN20 pipe, 20.6 m, ΔP≈15.4 kPa · £13/m × 20.6 m · install £272 · as-sized by connection_sizing (post-upsize) from 1.35 m3/h | PASS | 3 |  | PASS
243-PR-DN32 | Permeate Outlet | Cip Tank | DN32 | 4 m3/h | 1.148 | ≤3 m/s velocity | 44.97 | ✓ | 1580.98 | DN32 pipe, 45.0 m, ΔP≈19.6 kPa · £34/m × 45.0 m · install £1,529 · as-sized by connection_sizing (post-upsize) from 4 m3/h | PASS | 3 |  | PASS
244-PR-DN50 | Permeate Outlet | Ultrafiltration Module | DN50 | 8 m3/h | 1.027 | ≤3 m/s velocity | 21.23 | ✓ | 1103.04 | DN50 pipe, 21.2 m, ΔP≈4.6 kPa · £48/m × 21.2 m · install £1,019 · as-sized by connection_sizing (post-upsize) from 8 m3/h | PASS | 3 |  | PASS
245-PR-DN125 | Softener Vessel | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 7.46 | ✓ | 1229.8 | DN125 pipe, 7.5 m, ΔP≈0.5 kPa · £130/m × 7.5 m · install £970 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
246-PR-DN125 | Nutrient Tank | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 31.6 | ✓ | 4368 | DN125 pipe, 31.6 m, ΔP≈2.1 kPa · £130/m × 31.6 m · install £4,108 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
247-PR-DN125 | Distribution Manifold | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 32.61 | ✓ | 4499.3 | DN125 pipe, 32.6 m, ΔP≈2.1 kPa · £130/m × 32.6 m · install £4,239 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
248-PR-DN125 | Reverse Osmosis Skid | Drain Collection Sump | DN125 | 45 m3/h | 0.968 | ≤3 m/s velocity | 11.84 | ✓ | 1799.2 | DN125 pipe, 11.8 m, ΔP≈0.8 kPa · £130/m × 11.8 m · install £1,539 · as-sized by connection_sizing (post-upsize) from 45 m3/h | PASS | 3 |  | PASS
| Σ Process pipe lines | [7 empty] | 114084.12
Electrical & signal cables — current (A) · volt-drop limit ≤ 5 %
Basis note — common to the rows below (factored out of the per-row cells): cost model: model:uk-2026-supply+install
Tag | From | To | Size | Rating | Velocity / ΔU | Spec limit | Length (m) | In spec | Line £ | Basis | Row check | Audit: band | Audit: check evidence (build-computed) | Cell check
242-WT-DN20 | Mains Incomer | Standby Diesel Generator | 1.5 mm² | 4.2 A | 0.072 | ≤5% volt-drop | 10.17 | ✓ | 42.51 | 1 × 1.5 mm² Cu, 10.2 m · £3/m × 10.2 m · install £31 · volt-drop at 4.2 A over 10.17 m | PASS | 5 |  | PASS
243-PR-DN32 | Standby Diesel Generator | Transformer | 1.5 mm² | 4.2 A | 0.06 | ≤5% volt-drop | 8.4 | ✓ | 37.2 | 1 × 1.5 mm² Cu, 8.4 m · £3/m × 8.4 m · install £25 · volt-drop at 4.2 A over 8.4 m | PASS | 5 |  | PASS
244-PR-DN50 | Transformer | Main Switchboard | 1.5 mm² | 4.2 A | 0.042 | ≤5% volt-drop | 5.88 | ✓ | 29.64 | 1 × 1.5 mm² Cu, 5.9 m · £3/m × 5.9 m · install £18 · volt-drop at 4.2 A over 5.88 m | PASS | 5 |  | PASS
245-PR-DN125 | Main Switchboard | Motor Control Center | 1.5 mm² | 4.2 A | 0.142 | ≤5% volt-drop | 20 | ✓ | 72 | 1 × 1.5 mm² Cu, 20.0 m · £3/m × 20.0 m · install £60 · volt-drop at 4.2 A over 20.0 m | PASS | 5 |  | PASS
246-PR-DN125 | Motor Control Center | 3 Phase Power Input | 1.5 mm² | 4.2 A | 0.147 | ≤5% volt-drop | 5.73 | ✓ | 29.19 | 1 × 1.5 mm² Cu, 5.7 m · £3/m × 5.7 m · install £17 · volt-drop at 4.2 A over 5.73 m | PASS | 5 |  | PASS
247-PR-DN125 | Motor Control Center | Piping Network | 1.5 mm² | 4.2 A | 0.661 | ≤5% volt-drop | 25.84 | ✓ | 89.52 | 1 × 1.5 mm² Cu, 25.8 m · £3/m × 25.8 m · install £78 · volt-drop at 4.2 A over 25.84 m | PASS | 5 |  | PASS
248-PR-DN125 | Motor Control Center | Uv Disinfection | 1.5 mm² | 8.2 A | 1.236 | ≤5% volt-drop | 24.87 | ✓ | 86.61 | 1 × 1.5 mm² Cu, 24.9 m · £3/m × 24.9 m · install £75 · volt-drop at 8.2 A over 24.87 m | PASS | 5 |  | PASS
49 | Motor Control Center | Fertigation Dosing Pump | 1.5 mm² | 15 A | 2.145 | ≤5% volt-drop | 23.74 | ✓ | 83.22 | 1 × 1.5 mm² Cu, 23.7 m · £3/m × 23.7 m · install £71 · volt-drop at 15 A over 23.74 m | PASS | 5 |  | PASS
50 | Motor Control Center | Hand Watering Pump | 1.5 mm² | 4.2 A | 0.8 | ≤5% volt-drop | 31.25 | ✓ | 105.75 | 1 × 1.5 mm² Cu, 31.2 m · £3/m × 31.2 m · install £94 · volt-drop at 4.2 A over 31.25 m | PASS | 5 |  | PASS
51 | Motor Control Center | Drain Transfer Pump | 1.5 mm² | 3.9 A | 0.638 | ≤5% volt-drop | 27.34 | ✓ | 94.02 | 1 × 1.5 mm² Cu, 27.3 m · £3/m × 27.3 m · install £82 · volt-drop at 3.9 A over 27.34 m | PASS | 5 |  | PASS
52 | Motor Control Center | Cloth Filter | 1.5 mm² | 4.2 A | 0.543 | ≤5% volt-drop | 21.22 | ✓ | 75.66 | 1 × 1.5 mm² Cu, 21.2 m · £3/m × 21.2 m · install £64 · volt-drop at 4.2 A over 21.22 m | PASS | 5 |  | PASS
53 | Motor Control Center | Irrigation Pump | 1.5 mm² | 4.2 A | 0.718 | ≤5% volt-drop | 28.05 | ✓ | 96.15 | 1 × 1.5 mm² Cu, 28.0 m · £3/m × 28.1 m · install £84 · volt-drop at 4.2 A over 28.05 m | PASS | 5 |  | PASS
54 | Motor Control Center | Ro High Pressure Pump | 1.5 mm² | 8.4 A | 1.636 | ≤5% volt-drop | 32.43 | ✓ | 109.29 | 1 × 1.5 mm² Cu, 32.4 m · £3/m × 32.4 m · install £97 · volt-drop at 8.4 A over 32.43 m | PASS | 5 |  | PASS
55 | Motor Control Center | Gac Filter | 1.5 mm² | 4.2 A | 0.862 | ≤5% volt-drop | 33.68 | ✓ | 113.04 | 1 × 1.5 mm² Cu, 33.7 m · £3/m × 33.7 m · install £101 · volt-drop at 4.2 A over 33.68 m | PASS | 5 |  | PASS
56 | Motor Control Center | Permeate Outlet | 1.5 mm² | 4.2 A | 0.27 | ≤5% volt-drop | 10.54 | ✓ | 43.62 | 1 × 1.5 mm² Cu, 10.5 m · £3/m × 10.5 m · install £32 · volt-drop at 4.2 A over 10.54 m | PASS | 5 |  | PASS
57 | Motor Control Center | Concentrate Outlet | 1.5 mm² | 4.2 A | 0.193 | ≤5% volt-drop | 7.54 | ✓ | 34.62 | 1 × 1.5 mm² Cu, 7.5 m · £3/m × 7.5 m · install £23 · volt-drop at 4.2 A over 7.54 m | PASS | 5 |  | PASS
65 | Motor Control Center | Electrical Control Panel | 1.5 mm² | 4.2 A | 0.092 | ≤5% volt-drop | 3.59 | ✓ | 22.77 | 1 × 1.5 mm² Cu, 3.6 m · £3/m × 3.6 m · install £11 · volt-drop at 4.2 A over 3.59 m | PASS | 5 |  | PASS
66 | Electrical Control Panel | Digital Control Panel | 1.5 mm² | 0.5 A | 0.009 | ≤5% volt-drop | 2.89 | ✓ | 20.67 | 1 × 1.5 mm² Cu, 2.9 m · £3/m × 2.9 m · install £9 · volt-drop at 0.5 A over 2.89 m | PASS | 5 |  | PASS
67 | Motor Control Center | Control + Instrument UPS | 1.5 mm² | 4.2 A | 0.092 | ≤5% volt-drop | 3.62 | ✓ | 22.86 | 1 × 1.5 mm² Cu, 3.6 m · £3/m × 3.6 m · install £11 · volt-drop at 4.2 A over 3.62 m | PASS | 5 |  | PASS
68 | Control + Instrument UPS | Digital Control Panel | 1.5 mm² | 0.5 A | 0.008 | ≤5% volt-drop | 2.46 | ✓ | 19.38 | 1 × 1.5 mm² Cu, 2.5 m · £3/m × 2.5 m · install £7 · volt-drop at 0.5 A over 2.46 m | PASS | 5 |  | PASS
69 | Motor Control Center | SCADA / Plant Control System | 1.5 mm² | 4.2 A | 0.092 | ≤5% volt-drop | 3.26 | ✓ | 21.78 | 1 × 1.5 mm² Cu, 3.6 m · £3/m × 3.3 m · install £10 · volt-drop at 4.2 A over 3.26 m | PASS | 5 |  | PASS
70 | Motor Control Center | Digital Control Panel | 1.5 mm² | 0.5 A | 0.011 | ≤5% volt-drop | 3.54 | ✓ | 22.62 | 1 × 1.5 mm² Cu, 3.5 m · £3/m × 3.5 m · install £11 · volt-drop at 0.5 A over 3.54 m | PASS | 5 |  | PASS
71 | Piping Network | Digital Control Panel | 1.5 mm² | 0.5 A | 0.084 | ≤5% volt-drop | 26.99 | ✓ | 92.97 | 1 × 1.5 mm² Cu, 27.0 m · £3/m × 27.0 m · install £81 · volt-drop at 0.5 A over 26.99 m | PASS | 5 |  | PASS
72 | Motor Control Center | Electrical Control Cabinet | 1.5 mm² | 4.2 A | 0.718 | ≤5% volt-drop | 27.98 | ✓ | 95.94 | 1 × 1.5 mm² Cu, 28.0 m · £3/m × 28.0 m · install £84 · volt-drop at 4.2 A over 27.98 m | PASS | 5 |  | PASS
73 | Electrical Control Cabinet | Digital Control Panel | 1.5 mm² | 0.5 A | 0.087 | ≤5% volt-drop | 27.87 | ✓ | 95.61 | 1 × 1.5 mm² Cu, 27.9 m · £3/m × 27.9 m · install £84 · volt-drop at 0.5 A over 27.87 m | PASS | 5 |  | PASS
74 | Motor Control Center | Digital Control Panel | (unsized — no design current) | — | UNVERIFIED | ≤5% volt-drop (UNVERIFIED — no design current) | 3.83 | ✗ | 23.49 | power feeder, 3.8 m (design current unknown) · £3/m × 3.8 m · install £11 | FAIL — no carried current on the run; ΔU% missing — volt-drop unverifiable (dash is never in-spec) |  | no carried current on the run; ΔU% missing — volt-drop unverifiable (dash is never in-spec) | PASS
| Σ Electrical & signal cables | [7 empty] | 1580.13
| Rows FAILING the column contract (all sections, live count) | [6 empty] | 3

## Assembly sequence
Assembly & erection sequence — derived from this design | [6 empty] | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · arithmetic: min(8, 10 × 13/13 design-derived steps); content checks: design-derived step arithmetic — cell completeness+type contract 52/52 · score = min over checks of … · full audit: Quality & Audit tab
Order of works DERIVED FROM THE DESIGN: civils sized from the placed-plant footprint, one erection step per process region (GA order) with equipment grouped by module, pipework/electrical quantified from the connection schedule, and durations from the group counts × the unit norms footnoted below (ESTIMATE). Hold / witness points gate each step. A site-specific construction phase plan (CDM) is still required before works begin.
LARGEST LIFT: Fresh Water Tank [TK-108] at 656 kg (heaviest vessel mass in the bill of materials) → 20 t mobile crane (or lorry-mounted HIAB). Rule (ESTIMATE): crane rated ≥5× the load at a ~10 m working radius.
Step | Phase / activity | Scope — equipment groups (tags) | Predecessor | Lifting plant | Duration | Hold / witness point | Cell check
1 | Site set-out & civils | Ground-bearing slab 22.1 × 24.4 m (539.6 m², from the placed-plant footprint) + plinths, bunds & drainage falls | Site handover | Excavator, concrete pump | ~13.5 crew-days (ESTIMATE) | Set-out survey + concrete cube tests signed off | PASS
2 | Erect & set — Maintenance serviceability | Cip System X-101; Cip Tank TK-101; Cleaning Tank TK-102 | Civils complete & cured | 20 t mobile crane (or lorry-mounted HIAB) | ~1 crew-day (ESTIMATE) | Vessel hydrostatic (leak) test witnessed; machines: alignment + rotation (bump) test | PASS
3 | Erect & set — Mass fluid transport process | 8× Nutrient Tank TK-103, TK-104, TK-105, TK-109 (+4 more) — see GA; 2× Cloth Filter V-103, V-104; 2× Drain Collection Sump TK-114, TK-115; 2× Drain Transfer Pump P-104, P-105; 2× Drain Water Tank TK-106, TK-107; 2× Fertigation Dosing Pump P-106, P-107; 2× Softener Vessel V-106, V-107; Distribution Manifold M-101; Fresh Water Tank TK-108; Gac Filter V-101; (+9 more groups, 9 items — see GA) | Erect & set — Maintenance serviceability set | 20 t mobile crane (or lorry-mounted HIAB) | ~10 crew-days (ESTIMATE) | Vessel hydrostatic (leak) test witnessed; machines: alignment + rotation (bump) test | PASS
4 | Erect & set — Structure containment | Transformer TX-101 | Erect & set — Mass fluid transport process set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | Alignment + rotation (bump) test recorded | PASS
5 | Erect & set — Energy storage source | Main Switchboard EP-101; Mains Incomer EP-102 | Erect & set — Structure containment set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | Alignment + rotation (bump) test recorded | PASS
6 | Erect & set — Environmental interface | Concentrate Outlet X-103; Permeate Outlet X-104 | Erect & set — Energy storage source set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | Alignment + rotation (bump) test recorded | PASS
7 | Erect & set — Power distribution | 3 Phase Power Input D-101; Control + Instrument UPS U-201; Electrical Control Panel X-105; Motor Control Center EP-104; SCADA / Plant Control System EP-103; Standby Diesel Generator G-201 | Erect & set — Environmental interface set | Forklift / pallet truck | ~1.5 crew-days (ESTIMATE) | Alignment + rotation (bump) test recorded | PASS
8 | Erect & set — Control compute communication | Digital Control Panel I-103 | Erect & set — Power distribution set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | Alignment + rotation (bump) test recorded | PASS
9 | Erect & set — Safety protection | Electrical Control Cabinet I-102 | Erect & set — Control compute communication set | Forklift / pallet truck | ~0.5 crew-days (ESTIMATE) | Alignment + rotation (bump) test recorded | PASS
10 | Pipework & interconnections | 1021.9 m of sized pipe across 74 runs (DN125 512.2 m, DN150 139.1 m, DN20 20.6 m, DN25 (nominal — flow unknown) 23.9 m, DN32 133.9 m, DN50 104.1 m) — per the connection schedule / Line & velocity tab | Equipment set & grouted | Pipe trolleys, chain hoists | ~41 crew-days (ESTIMATE) | Pressure / leak test certificate per line | PASS
11 | Electrical installation | 422.7 m of LV cable per the connection schedule; boards & distribution per the Electrical tab (single-line + panel schedule) | Cable routes / trays installed | Cable drum jacks | ~7.5 crew-days (ESTIMATE) | Insulation-resistance + earth-continuity tests | PASS
12 | Instrumentation, controls & SCADA | 51 instrument loop(s) from the bill of materials — mount, hook-up, loop-check | Electrical energised (LV) | Hand tools | ~6.5 crew-days (ESTIMATE) | Loop checks + calibration certificates | PASS
13 | Pre-commissioning & commissioning | Whole plant — flush, fill, leak-check, energise, wet-commission, performance test (48 principal items) | All systems installed & tested | — | ~10 crew-days (ESTIMATE) | Water-on, functional + performance test; client witness | PASS
Duration norms used above — stated, industry-plausible defaults (ESTIMATE, not design-derived)
| civils: 40 m² slab per crew-day | ESTIMATE — ground-bearing slab + plinths/bunds, incl. set-out & cure wait overlap
| vessel: 3 vessel lifts per crane-day | ESTIMATE — set, level, grout & hold — light vessels (<5 t) on a mobile crane
| machine: 4 items per crew-day | ESTIMATE — skid/machine set + alignment on prepared plinths
| pipe: 25 m installed & tested per crew-day | ESTIMATE — carbon/PE process pipe incl. supports, per 2-fitter crew
| cable: 60 m pulled & terminated per crew-day | ESTIMATE — LV power/control cable on tray, per 2-electrician crew
| loop: 8 instrument loops per crew-day | ESTIMATE — mount, hook-up, loop-check & calibration certificate
| commission: 10 principal items per day + 5 days flat | ESTIMATE — flush/fill/leak-check, energise, wet-commission, performance test

## Risk & Regulatory
Risk & Regulatory | [12 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · column-contract arithmetic: 10 × 10/10 rows passing; content checks: risk-register column contract (per-row triage) — cell completeness+type contract 184/184 · score = m… · full audit: Quality & Audit tab
Preliminary hazard & risk register PLUS the regulatory / compliance duties, on one sheet (both derive from the same universal hazard library). Risk rows come LIVE from the physics critic, the deterministic gate flags, the cost-sanity check and the equipment present; the regulatory section adds the engine's compliance-gate verdict and the jurisdiction × hazard → regulation matrix. Score = S × L (≤7 Low / 8–14 Medium / ≥15 High). Every row is TRIAGED from its own provenance + content: an ENGINE-FIXABLE row (a design defect the engine controls — sizing / spec / coverage / consistency) is an OPEN DEFECT that names its routed fix stage and can never ship as 'tolerable with mitigation'; only a genuinely EXTERNAL risk (inherent process hazard, site / utility / supply-chain / regulatory factor) carries a mitigation. Universal — not plant-specific. Preliminary; a site-specific HAZID / HAZOP and a regulatory review are required before construction / sale. ROW CHECK CONTRACT (score = 10 × rows-passing ÷ rows = 10 × 10/10 = 10.0): Class=computed · Mitigation / fix route=required_nonempty · Residual=computed. A dash / empty / unverifiable contracted cell FAILS its row — honest red beats fake green.
Risk register
# | Category | Hazard / finding | Cause | S | L | Score | Rating | Class | Mitigation / fix route | Residual | Source | Row check | Audit: check evidence (build-computed triage) | Cell check
1 | Engineering — design | ADVISORY (uncorroborated by deterministic check — visible, never scores): The UV Disinfection unit is rated at 4 kW but is housed in a 600x510x660 mm envelope, which is physically too small for a 4 kW multi-lamp UV reactor designed to handle high flow rates. | Physics critic (engineering_plausibility), at modules[1].sub_modules[0].words[25]. | 3 | 3 | 9 | Medium | EXTERNAL | Physics-critic I/O artifact — not a design property (gate-33 false-positive discipline); re-run Stage 7.5 to clear. | Tolerable (with mitigation) | state.physicsCritique.issues | PASS |  | PASS
2 | Engineering — design | ADVISORY (uncorroborated by deterministic check — visible, never scores): The GAC Filter is listed with a capacity of 1.8 m³ and dimensions of 1.3 m dia x 1.4 m, which is significantly smaller than the 42-inch (1.06 m) diameter by 1.8 m height tank implied by the brief's 14.5 m³/h capacity. | Physics critic (brief_to_design_fidelity), at modules[1].sub_modules[0].words[111]. | 2 | 3 | 6 | Low | EXTERNAL | Physics-critic I/O artifact — not a design property (gate-33 false-positive discipline); re-run Stage 7.5 to clear. | Tolerable (with mitigation) | state.physicsCritique.issues | PASS |  | PASS
3 | Process safety / HSE | Toxic / asphyxiant gas release | Biological or chemical processes can release ammonia, hydrogen sulphide or chlorine. | 4 | 2 | 8 | Medium | EXTERNAL | Gas detection, forced ventilation, scrubbing, respiratory PPE, confined-space controls. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
4 | Process safety / HSE | Stored pressure energy | Pressurised vessels and lines can fail explosively. | 4 | 2 | 8 | Medium | EXTERNAL | Design + periodic inspection to pressure code, relief devices, written scheme of examination. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
5 | Process safety / HSE | Rotating machinery — entanglement / mechanical failure | Exposed rotating parts; stored mechanical energy; loss of a duty machine upsets the process. | 3 | 3 | 9 | Medium | EXTERNAL | Fixed guarding, lock-off / isolation (LOTO), N+1 standby on critical duties, vibration monitoring. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
6 | Process safety / HSE | Electrical — shock / arc-flash | High fault energy at switchgear and transformers; shock risk from LV / HV. | 4 | 2 | 8 | Medium | EXTERNAL | BS 7671 installation, arc-flash assessment, lock-off, IP-rated enclosures, RCD + earthing. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
7 | Process safety / HSE | Working at height / confined space (tanks & vessels) | Tank tops present a fall risk; tank interiors are confined spaces (atmosphere / drowning). | 4 | 2 | 8 | Medium | EXTERNAL | Edge protection, confined-space permit-to-work, atmosphere testing, rescue plan. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
8 | Process safety / HSE | Environmental discharge to controlled waters | Process effluent or sludge discharged to controlled waters requires consent. | 3 | 3 | 9 | Medium | EXTERNAL | Discharge permit, effluent treatment to consent limits, monitoring + reporting. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
9 | Process safety / HSE | Chemical handling — corrosive / reactive | Dosing chemicals are corrosive or reactive; incompatible mixing is hazardous. | 3 | 2 | 6 | Low | EXTERNAL | Bunding, segregated storage, COSHH assessment, PPE, eyewash / safety shower. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
10 | Process safety / HSE | Radiation — ultraviolet / ozone exposure | Ultraviolet reactors emit harmful UV; ozone is a respiratory irritant. | 2 | 2 | 4 | Low | EXTERNAL | Interlocked enclosures, UV-opaque shielding, ozone detection + destruct. | Tolerable (with mitigation) | Equipment present in the bill of materials | PASS |  | PASS
Regulatory & compliance
Jurisdiction: UK · compliance-gate verdict: WARN (0/0 class standards covered). Statutory duties below are derived from the jurisdiction + the hazards present (universal matrix), not a per-class list — verify before sale / construction.
Engine compliance-gate verdict
WARN | No class-standards registered for "water_treatment". Compliance check skipped — engineer must verify manually before sale.
Statutory duties that always apply (UK)
# | Regulation / standard | Applies because | Status | Cell check
1 | Health and Safety at Work etc. Act 1974 | Overarching duty of care to workers and others. | Mandatory — verify | PASS
2 | Management of Health and Safety at Work Regulations 1999 | Suitable & sufficient risk assessment. | Mandatory — verify | PASS
3 | Construction (Design and Management) Regulations 2015 (CDM) | Design + construction safety duties. | Mandatory — verify | PASS
4 | Supply of Machinery (Safety) Regulations 2008 (UKCA) | Machinery conformity + UKCA marking. | Mandatory — verify | PASS
Hazard-driven regulations (from the equipment present)
# | Regulation / standard | Triggered by (hazard present) | Status | Cell check
1 | Control of Substances Hazardous to Health Regulations 2002 (COSHH) | Toxic / asphyxiant gas release; Chemical handling — corrosive / reactive | Mandatory — verify | PASS
2 | Pressure Systems Safety Regulations 2000 (PSSR) | Stored pressure energy | Mandatory — verify | PASS
3 | Pressure Equipment (Safety) Regulations 2016 | Stored pressure energy | Mandatory — verify | PASS
4 | Provision and Use of Work Equipment Regulations 1998 (PUWER) | Rotating machinery — entanglement / mechanical failure | Mandatory — verify | PASS
5 | Supply of Machinery (Safety) Regulations 2008 (UKCA) | Rotating machinery — entanglement / mechanical failure | Mandatory — verify | PASS
6 | Electricity at Work Regulations 1989 | Electrical — shock / arc-flash | Mandatory — verify | PASS
7 | BS 7671 Requirements for Electrical Installations | Electrical — shock / arc-flash | Mandatory — verify | PASS
8 | Work at Height Regulations 2005 | Working at height / confined space (tanks & vessels) | Mandatory — verify | PASS
9 | Confined Spaces Regulations 1997 | Working at height / confined space (tanks & vessels) | Mandatory — verify | PASS
10 | Environmental Permitting (England and Wales) Regulations 2016 | Environmental discharge to controlled waters | Mandatory — verify | PASS
11 | Dangerous Substances and Explosive Atmospheres Regulations 2002 (DSEAR) | Chemical handling — corrosive / reactive | Mandatory — verify | PASS
12 | Control of Artificial Optical Radiation at Work Regulations 2010 | Radiation — ultraviolet / ozone exposure | Mandatory — verify | PASS

## Holds & exclusions
Holds & exclusions — the honest open-items register |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · live-derivation check (each hold re-derived from the current contract results) — rendered holds match the LIVE re-derivation (stale hold = fail) 5/5; cell completeness+t… · full audit: Quality & Audit tab
Every hold is DERIVED LIVE from a failing check or column contract at build time — never hand-typed — so this register is always current: fix the item at source, rebuild, and its hold disappears. The dossier ships as a draft WITH these holds against it; the exclusions restate what was never in scope.
HOLDS — 5 open item(s), numbered
Hold | Item | Scope (live count) | Derived from | Clears when | Cell check
HOLD-001 | Line sizing pending flow allocation | 2 line(s) with no derivable flow (velocity unverifiable) | Line & velocity column contract (live per-row evaluation) | author the real flow demand on every fluid topology edge at source — the contract then re-passes and this hold clears | PASS
HOLD-002 | Bought-out manufacturer part numbers pending detailed design | 32/70 engineered bought-out lines carry an explicit 'TBD (detailed design)' part number (commodity lines 'MPN at procurement' are tallied separately and carry no hold: 17) | Bill of Materials ledger column contract (live TBD count) | resolve real MPNs at detailed design (Stage 17.6 library / supplier RFQs) — the TBD count then falls and this hold clears | PASS
HOLD-003 | Panel circuits failing the schedule column contract | 1/23 circuit row(s) FAIL (missing ΔU / out-of-band volt-drop) | Panel schedule column contract (live per-circuit evaluation) | route + size the failing circuits so ΔU computes in-band | PASS
HOLD-004 | Needs input — coverage_partial | 6 drawing(s) partially covered (worst 75%): process-schedules: 18/24; panel-schedule: 20/23; block-flow-diagram: 16/18; pid: 38/42 — minor over-decomposition detail; principal syst | self-repair loop (severity MED, tab Coverage) | each engineering drawing must represent every PRINCIPAL part; minor decomposition detail may be represented by its parent ¦ repair: no deterministic single-answer fix — human / sou | PASS
HOLD-005 | Needs input — advisory_critic_notes | 2 critic note(s) are UNCORROBORATED by any deterministic check over the delivered artefacts — rendered as advisory, never scored: The UV Disinfection unit is rated at 4 kW but is h | self-repair loop (severity INFO, tab Risk & Regulatory) | a critic finding may score only when corroborated by a deterministic check over delivered artefacts (B3 finding-set extension) ¦ repair: no deterministic single-answer fix — human | PASS
EXCLUSIONS — never in this plant's scope
• the grow-lighting / assimilation lighting and its switchboards
• the climate / heating, ventilation and cooling hardware and the climate-control computer
• the cultivation rack framework
• the building, civil works and excavation
• the main electrical switchboard and the feeder cables to it, and earthing/cable tray/cable penetrations

## Questions for the customer
Questions for the customer — confirm or correct |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · live-derivation check (each question re-derived from the run's own artefacts: brief augmentation, plausibility critic, decisions register, client-offer reconciliation) —… · full audit: Quality & Audit tab
Customers don't know what they want — so every value the engine had to assume, every brief field still missing, every physics contradiction and every unexplained divergence from your offer is a NUMBERED QUESTION here. Each row is derived live from a named engine artefact at build time (never hand-typed): answer it in the brief or record a scope decision, rebuild, and the row disappears. What changes if your answer differs is stated per row.
OPEN QUESTIONS — 5, numbered (each names the artefact that raised it)
Q# | Question for the customer | Why it matters — what changes if the answer differs | Assumption in force (until answered) | Provenance (engine artefact that raised it) | Cell check
Q-001 | What is the required max mass kg? The brief does not state it and no class default exists. | a stated mass cap becomes a hard constraint on the skid/structure and the transport & lifting plan; today nothing bounds the plant's shipped mass | none in force — the field is empty in the design basis; the design proceeds unconstrained on it | brief augmentation (still_missing) — 1-parsed-brief-augmented.json | PASS
Q-002 | What is the required operating environment? The brief does not state it and no class default exists. | the ambient min/max drive thermal sizing (heater/chiller duty, derating), material selection and IP ratings; today no ambient-envelope check can run | none in force — the field is empty in the design basis; the design proceeds unconstrained on it | brief augmentation (still_missing) — 1-parsed-brief-augmented.json | PASS
Q-003 | We assumed target process = Continuous chemical process: capture; field-erected fixed plant with closed-loop solvent/reagent recovery and automated… — confirm or correct. | every quantity derived from this field moves if the real value differs (it entered the design as if the brief had stated it) | inferred: Continuous chemical process: capture; field-erected fixed plant with closed-loop solvent/reagent re… — Process inferred from brief mission/description for water_treatment. class-agnostic inference from brief text for unmapped class 'water_tre… | brief augmentation (was_filled) — 1-parsed-brief-augmented.json | PASS
Q-004 | Please review: For each thin sub-module: confirm whether it should be split further OR accept that the sub-module is genuinely a single-component unit. | A thin sub-module may indicate the chain missed components OR that the sub-module truly is simple (e.g. a single moulded enclosure). Without human review you can't tell which. | grammar: 7 sub-module(s) UNDER-DENSE (<5 words; need 5-7 for a real BoM): fertigation_dosing_system::fertigation_dosing_system__primary_assembly (1 words), sensing_instrumentation::sensing_instrument… | design-decisions register — gate-unrepaired::sub_module_word_density (unrepaired_gate, module fertigation_dosing_system) | PASS
Q-005 | Please review: Trim the module overview to only describe what exists in the design data. | Inflated prose creates the false impression of completeness. Same readability concern. | grammar: 2 module(s) name components in overview that are absent from sub-modules (procurement gap): mass_fluid_transport_process: overview mentions 3 concrete components not present in any sub-modul… | design-decisions register — gate-unrepaired::module_prose_subset_of_sub_modules (unrepaired_gate, module mass_fluid_transport_process) | PASS

## Quality & Audit
Quality & Audit — every section and tab against the ≥8 floor + the ship gate |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · THE dossier floor — min score of every deterministic section & non-mirror tab (identical to the verdict computation); own content check: floor mirror + audit-surface int… · full audit: Quality & Audit tab
The engine's own quality surface, on one tab: the dossier verdict (stated ONCE, here), every DETERMINISTIC section and every tab scored against the ≥8 floor (the LLM self-audit's opinions render as advisory annotations — visible, never scoring; B3), and the deterministic ship-gate audit findings. The AIM is ≥8 EVERYWHERE — the floor, not the average. See ⚠ Checks for the live arithmetic invariants.
VERDICT: SHIPS · floor 8/10 (min of every DETERMINISTIC section & non-mirror tab — live cells on Quality & Audit; the LLM self-audit is advisory and never floors; ships at ≥8 everywhere)
MIN deterministic section score —/10 |  | 0/0 deterministic sections ≥8 | LLM self-audit min 5/10 — ADVISORY, uncorroborated; annotates, never floors (B3) · AIM: every section ≥8
Section | Score (deterministic) | vs ≥8 floor | Self-audit opinion (advisory — never floors) | Top defect (why it's below 8) | Cell check
Headline (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 9 — advisory, uncorroborated |  | PASS
Brief compliance (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 8 — advisory, uncorroborated |  | PASS
Bill of materials (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 7 — advisory, uncorroborated | 5 genuinely unpriced lines (terminal blocks etc.) | PASS
Performance card (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 10 — advisory, uncorroborated |  | PASS
Design narrative (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 8 — advisory, uncorroborated |  | PASS
Physics fidelity (advisory) | — (no deterministic section — the deliverable is scored on the per-tab table below) | ADVISORY — non-gating | self-audit opinion: 5 — advisory, uncorroborated | HIGH severity sizing discrepancy on softener vessels/pumps | PASS
Engine quality metrics — the dossier's own confidence rating
Deterministic sections at ≥8 (AIM: all) | 0 / 0 |  | AIM: 100%
Min deterministic section score (floors) | —/10
Min self-audit opinion (advisory — never floors) | 5/10 |  | AIM: 100%
Traceability — every number → the brief | 100% |  | AIM: 100%
Calc-coverage — every number shows its formula | 69% |  | AIM: 100%
Per-tab quality — every tab against the ≥8 floor (worst: Executive Summary 8.0/10; 0 FAIL, 0 UNSCORED). Score = live formula; muted 'Audit:' columns hold the embedded score operands (passed/checked per component + the governing cap).
Tab | Score | vs ≥8 floor | Top issue / coverage gap (fix at source) | Basis — mechanism & caps (stated) | Audit: governing cap | Audit: p1 | Audit: c1 | Audit: p2 | Audit: c2 | Audit: p3 | Audit: c3 | Audit: p4 | Audit: c4 | Audit: p5 | Audit: c5 | Cell check
Executive Summary | 8 | PASS ✓ | capped at the dossier FLOOR (8/10): the cover cannot claim a higher score than its weakest sheet — fix that sheet to raise this one | MIRROR of the dossier floor (min of every deterministic section & non-mirror tab) — re-stamped from the CURRENT scores, never a stale earlier cap; own content check: cover compliance arithmetic (achieved vs target re-evaluated per row) — brief-compli | 10 | [10 empty] | PASS
Quality & Audit | 8 | PASS ✓ |  | THE dossier floor — min score of every deterministic section & non-mirror tab (identical to the verdict computation); own content check: floor mirror + audit-surface integrity (rows tie to the live scorecard) — per-tab table rows name real scored tab | 10 | [10 empty] | PASS
Overview | 10 | PASS ✓ |  | dashboard integrity (every quoted number vs its engine source) — capex category % = 100 × £ / Σ (per-row arithmetic) 10/10; Σ capex categories ≈ the BoM materials total 1/1; cell completeness+type contract 51/51 · score = min over checks of 10 × pass | 10 | 10 | 10 | 1 | 1 | 51 | 51 |  |  |  |  | PASS
Brief | 10 | PASS ✓ |  | client-offer reconciliation (live section mapping) — client-offer reconciliation sections consistent (incl. decision-covered) 6/6; every live section rendered as a reconciliation row 1/1; cell completeness+type contract 20/20 · score = min over check | 10 | 6 | 6 | 1 | 1 | 20 | 20 |  |  |  |  | PASS
Quantities | 10 | PASS ✓ |  | quantity provenance (source + where-from + used-by per row) — provenance-verified quantity rows 113/113; cell completeness+type contract 339/339 · score = min over checks of 10 × passed/checked | 10 | 113 | 113 | 339 | 339 | [6 empty] | PASS
Calculations | 10 | PASS ✓ |  | worked-calc coverage (every definition resolves to a computed result; inputs populated) + tool-flow consumption — worked-calc definitions resolve to a computed result 13/13; calc input rows carry their value 37/37; tool outputs consumed downstream 37 | 10 | 13 | 13 | 37 | 37 | 37 | 37 | 223 | 223 |  |  | PASS
Bill of Materials (Ledger) | 8 | PASS ✓ | 32/70 ENGINEERED bought-out lines carry MPN 'TBD (detailed design)' — an ESTIMATE-stage gap; score = arithmetic − 4 × engineered-TBD-fraction = 10.0 − 1.8 (17 commodity line(s) 'MPN at procurement' tallied separately, unpenalised) | column-contract arithmetic: 10 × 435/435 rows passing; content checks: BoM ledger column contract (per-row Row check) — cell completeness+type contract 3038/3061 · score = min over checks of 10 × passed/checked | 8 | 3038 | 3061 | [8 empty] | PASS
Cost waterfall | 10 | PASS ✓ |  | cost-waterfall arithmetic ties (each step vs its named costStack anchor; sums close) — waterfall rows tie live to their stated costStack anchor 6/6; assembly/install rows computed live from their factors 7/7; Σ class subtotals ≈ the BoM materials tot | 10 | 6 | 6 | 7 | 7 | 1 | 1 | 67 | 67 |  |  | PASS
Financial model | 8.7 | PASS ✓ | 30 orphan numeric literal(s) in the financial model (e.g. row 35 col 2, row 35 col 3, row 36 col 2, row 36 col 3) — a model number must be driven, not typed | formula integrity (cells reference drivers; no orphan literals) + scenario arithmetic (live) — model value cells are live formulas or declared (yellow) inputs 193/223; cell completeness+type contract 389/389 · score = min over checks of 10 × passed/c | 10 | 193 | 223 | 389 | 389 | [6 empty] | PASS
Connection trace | 10 | PASS ✓ |  | resolved-endpoint fraction (every ← / → tag must exist) + per-row status — connection rows carry a computed OK status (0 unresolved endpoints, no missing-tie evidence) 48/48; cell completeness+type contract 106/106 · score = min over checks of 10 × p | 10 | 48 | 48 | 106 | 106 | [6 empty] | PASS
Part names | 8 | PASS ✓ | cell contract: 1 of 392 required cells empty/invalid across 1 row(s) — e.g. row 75: 'Tag' placeholder '—' | dedupe + completeness (every BoM tag present exactly once) — part tags unique (each physical thing named once) 107/107; cell completeness+type contract 391/392 · score = min over checks of 10 × passed/checked | 8 | 107 | 107 | 391 | 392 | [6 empty] | PASS
Risk & Regulatory | 10 | PASS ✓ |  | column-contract arithmetic: 10 × 10/10 rows passing; content checks: risk-register column contract (per-row triage) — cell completeness+type contract 184/184 · score = min over checks of 10 × passed/checked | 10 | 184 | 184 | [8 empty] | PASS
Assembly sequence | 8 | PASS ✓ | 13/13 steps carry design-derived content (footprint / region groups / schedule quantities / BoM lift mass); duration norms are stated ESTIMATE defaults — capped at 8 until the norms themselves are design-derived | arithmetic: min(8, 10 × 13/13 design-derived steps); content checks: design-derived step arithmetic — cell completeness+type contract 52/52 · score = min over checks of 10 × passed/checked | 8 | 52 | 52 | [8 empty] | PASS
Process schedules | 8 | PASS ✓ | cell contract: 85 of 454 required cells empty/invalid across 44 row(s) — e.g. row 9: 'Size' placeholder '—'; 'Set / Cv' placeholder '—'; 'Fail' placeholder '—' | schedule column contract (per-cell completeness + type over every schedule row, from the drawings/*.md source) — cell completeness+type contract 369/454 · score = min over checks of 10 × passed/checked | 8 | 369 | 454 | [8 empty] | PASS
Line & velocity | 9.6 | PASS ✓ | 3/74 rows FAIL the column contract (arithmetic score 10 × 71/74 = 9.6) — e.g. Fresh Water Tank→Nutrient Tank: velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint · Fresh Water Tank→Drain Water Tank: velocity underivable — no flow demand on the edge and no contract flow/throughput quantity matches either endpoint · Motor Control Center→Digital Control Panel: no carried current on the run | column-contract arithmetic: 10 × 71/74 rows passing; content checks: line & velocity column contract (per-row Row check) — cell completeness+type contract 518/518 · score = min over checks of 10 × passed/checked | 10 | 518 | 518 | [8 empty] | PASS
Glossary | 10 | PASS ✓ |  | glossary contract (every term defined + no orphan terms) — every rendered term carries a definition 47/47; terms actually used somewhere in the workbook 47/47 · score = min over checks of 10 × passed/checked | 10 | 47 | 47 | 47 | 47 | [6 empty] | PASS
Electrical | 9.6 | PASS ✓ | 1/23 circuit/board/drawing rows FAIL the column contract (arithmetic score 10 × 22/23 = 9.6) — e.g. single-line ↔ schedule · board hierarchy: board reference(s) absent from the single-line drawing: MAIN DISTRIBUTION BOARD (TP&N) | column-contract arithmetic: 10 × 22/23 rows passing; content checks: panel-schedule column contract + single-line drawing coverage — cell completeness+type contract 187/187 · score = min over checks of 10 × passed/checked | 10 | 187 | 187 | [8 empty] | PASS
Design basis | 8 | PASS ✓ | 26/26 basis lines carry a value + a named source (module constant / contract quantity / live Inputs cell); capped at 8 — a derived statement of basis, not an independently verified document | arithmetic: min(8, 10 × 26/26 complete rows); content checks: design-basis completeness arithmetic — cell completeness+type contract 104/104 · score = min over checks of 10 × passed/checked | 8 | 104 | 104 | [8 empty] | PASS
Holds & exclusions | 8 | PASS ✓ | 5 open hold(s) + 5 exclusion(s) — every hold derived live from a failing check/contract (TBD / out-of-scope items disclosed, not hidden); capped at 8 while any hold is open | live-derivation check (each hold re-derived from the current contract results) — rendered holds match the LIVE re-derivation (stale hold = fail) 5/5; cell completeness+type contract 25/25 · score = min over checks of 10 × passed/checked | 8 | 5 | 5 | 25 | 25 | [6 empty] | PASS
Questions for the customer | 10 | PASS ✓ | 5 open question(s) for the customer — every row derived live from a named engine artefact (brief augmentation / plausibility critic / decisions register / client-offer reconciliation); an answered question disappears on rebuild | live-derivation check (each question re-derived from the run's own artefacts: brief augmentation, plausibility critic, decisions register, client-offer reconciliation) — rendered questions match the LIVE re-derivation (stale/dropped question = fail) | 10 | 5 | 5 | 25 | 25 | [6 empty] | PASS
⚠ Checks | 10 | PASS ✓ | 308/308 invariants pass | fail-count formula: 10 if 0 FAIL else max(0, 8 − 2 × fails) — deterministic invariants pass 7/7; cell completeness+type contract 197/197 · score = min over checks of 10 × passed/checked | 10 | 7 | 7 | 197 | 197 | [6 empty] | PASS
Renders | 9.7 | PASS ✓ | Render part coverage 29/30 (97%) | render mechanism: parts-ledger coverage × default-size litter × typed-shape × vision-critic verdict (render-vision-critique.json) — drawing part coverage (blender) 29/30 · score = min over checks of 10 × passed/checked | 10 | 29 | 30 | [8 empty] | PASS
GA — General Arrangement | 9.7 | PASS ✓ | GA part coverage 29/30 (97%) | GA mechanism: parts-ledger coverage × default-size litter × layout-divergence × typed-shape checks — drawing part coverage (general-arrangement) 29/30 · score = min over checks of 10 × passed/checked | 10 | 29 | 30 | [8 empty] | PASS
P&ID | 9 | PASS ✓ | P&ID part coverage 38/42 (90%) | P&ID part-coverage arithmetic (parts_ledger ✓/✗ vs the BoM) — drawing part coverage (pid) 38/42 · score = min over checks of 10 × passed/checked | 9 | 38 | 42 | [8 empty] | PASS
BFD — Block Flow | 8.9 | PASS ✓ | Block-flow part coverage 16/18 (89%) | block-flow part-coverage arithmetic (parts_ledger) — drawing part coverage (block-flow-diagram) 16/18 · score = min over checks of 10 × passed/checked | 10 | 16 | 18 | [8 empty] | PASS
HVAC | 8 | PASS ✓ | HVAC is OUT OF SCOPE for this process / fluid plant — its climate hardware (heating / ventilation / cooling) is supplied by others (per the brief); the sheet honestly documents building-ventilation only, with no HVAC equipment to size or mis-represent. Class-appropriate, not a coverage gap. | HVAC duty-scoped check: contract duty signal → drawing coverage; no duty → honest out-of-scope disclosure (capped 8) | 8 | [10 empty] | PASS
Drawings | 8 | PASS ✓ | 4 drawing(s) registered with 20 print-ready A1 sheet PDF(s), all present on disk, lettering ≥2.5 mm | drawing-register integrity: every registered A1 print PDF exists on disk + ISO 3098 2.5 mm lettering bar — registered drawings with their print set present 4/5; registered render views with a file 8/8; cell completeness+type contract 48/49 · score = | 10 | 4 | 5 | 8 | 8 | 48 | 49 |  |  |  |  | PASS
Sense-check | 10 | PASS ✓ |  | generative benchmark sanity net (gate 36): independent top-down LLM expectation diffed against the bottom-up engine, per-dimension — benchmark dimensions within the expectation envelope 6/6; gate-36 verdict is not RADICAL 1/1; cell completeness+type | 10 | 6 | 6 | 1 | 1 | 47 | 47 |  |  |  |  | PASS
Inputs & Assumptions | 10 | PASS ✓ |  | driver integrity (every input driver consumed by a live formula) — drivers referenced by a live formula somewhere 18/18; cell completeness+type contract 54/54 · score = min over checks of 10 × passed/checked | 10 | 18 | 18 | 54 | 54 | [6 empty] | PASS
Audit data | 10 | PASS ✓ |  | audit-operand register contract (every embedded operand carries its label + provenance; per-row Cell check formulas) — cell completeness+type contract 100/100 · score = min over checks of 10 × passed/checked | 10 | 100 | 100 | [8 empty] | PASS
Contents | 10 | PASS ✓ |  | index integrity (both directions) — index rows point at an existing tab 30/30; every sheet listed in the index 30/30; cell completeness+type contract 90/90 · score = min over checks of 10 × passed/checked | 10 | 30 | 30 | 30 | 30 | 90 | 90 |  |  |  |  | PASS
LIVE FLOOR — min of every deterministic section & non-mirror tab (the ONE VERDICT's number, computed in-cell) | 8
LIVE OPEN ISSUES — sections/tabs below 8 or unscored (computed in-cell over the same score cells) | 0
⚠ Deterministic ship-gate audit — every per-tab check (no LLM)
Findings: 0 HIGH · 1 MED · 0 LOW · 1 total — a HIGH finding means the dossier is NOT validated.
Coverage
Severity | Check | Message | Actual | Expected | Cell check
MED | coverage_partial | 6 drawing(s) partially covered (worst 75%): process-schedules: 18/24; panel-schedule: 20/23; block-flow-diagram: 16/18; pid: 38/42 — minor over-decomposition detail; principal systems are represented | 6 partial drawings, worst 75% | every principal system represented on each drawing (≥95% coverage) | PASS
Risk & Regulatory
Severity | Check | Message | Actual | Expected | Cell check
INFO | advisory_critic_notes | 2 critic note(s) are UNCORROBORATED by any deterministic check over the delivered artefacts — rendered as advisory, never scored: The UV Disinfection unit is rated at 4 kW but is housed in a… ¦ The GAC Filter is listed with a capacity of 1.8 m³ and dimensions of… | 2 advisory notes | advisory notes are visible but carry no score penalty | PASS
BENCHMARK NET — independent generative-LLM expectation (top-down) vs the engine (bottom-up)
deterministic output deviates from the benchmark — review recommended · model: z-ai/glm-5.2 · worst verdict: warn
Dimension | LLM expected (top-down) | Engine (bottom-up) | Ratio | Verdict / note | Cell check
all-in cost | £800,000–1,500,000 (mid £1,100,000) | £1,132,439 (costStack.oem_transfer_price_gbp) | 1.03× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type
output — irrigation_demand | 45 m³/h | 90 m³/h (contract.irrigation_demand_m3_h) | 2.00× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type
output — ro_permeate_capacity | 8 m³/h | 8 m³/h (contract.ro_permeate_capacity_m3_h) | 1.00× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type
output — water_storage_capacity | 120 m³ | 120 m3 (contract.water_storage_delivered_m3) | 1.00× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type
output — actuated_valves | 200 count | 200 count (contract.actuated_distribution_valve_count) | 1.00× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type
output — ro_recovery | 75 % | 75 % (contract.ro_recovery_percent) | 1.00× |  | ⚠ FAIL — a required cell is empty/placeholder or wrong type

## Sense-check
Independent sense-check — generative LLM expectation vs the deterministic engine
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · generative benchmark sanity net (gate 36): independent top-down LLM expectation diffed against the bottom-up engine, per-dimension — benchmark dimensions within the expe… · full audit: Quality & Audit tab
An LLM independently estimates, TOP-DOWN from the market, what a plant like this should cost, output and be built from. The deterministic engine builds BOTTOM-UP from parts. The two methods are diffed: a large gap means one is wrong. This is the engine's own sanity check — shown here so you can see it, not just trust it.
SENSE-CHECK VERDICT: WARN |  |  |  | deterministic output deviates from the benchmark — review recommended
All-in cost — LLM top-down envelope vs the engine
| LLM expected (top-down) | Engine (bottom-up) | Ratio | Basis | Cell check
All-in cost | £800,000–£1,500,000 (mid £1,100,000) | £1,132,439 | 1.0× | Commercial cultivation fertigation + water treatment systems typically run £130–250 per plant container fully installed; 6000 containers → £0.8–1.5M, with 200 actuated valves and 120 m³ storage pushing toward mid-high end. | PASS
Per-dimension divergence — 6 checked (cost · output · sizing · components)
Dimension | LLM expected | Engine (deterministic) | Ratio | Verdict | Cell check
all-in cost | £800,000–1,500,000 (mid £1,100,000) | £1,132,439 (costStack.oem_transfer_price_gbp) | 1.0× | ok | PASS
output — irrigation_demand | 45 m³/h | 90 m³/h (contract.irrigation_demand_m3_h) | 2.0× | warn | PASS
output — ro_permeate_capacity | 8 m³/h | 8 m³/h (contract.ro_permeate_capacity_m3_h) | 1.0× | ok | PASS
output — water_storage_capacity | 120 m³ | 120 m3 (contract.water_storage_delivered_m3) | 1.0× | ok | PASS
output — actuated_valves | 200 count | 200 count (contract.actuated_distribution_valve_count) | 1.0× | ok | PASS
output — ro_recovery | 75 % | 75 % (contract.ro_recovery_percent) | 1.0× | ok | PASS
Per-line-item faults — 7 lines the LLM flags as wrong in the engine's bill
Bill line | What's wrong | Magnitude | LLM-suggested | Likely cause | Cell check
P-103 | Irrigation pump sized at 90 m³/h | 2× oversized | 45 m³/h pump | contract.irrigation_demand_m3_h set to 90 instead of benchmark 45 | PASS
— ¦ qty 8280 ¦ unit £13.2 | Zoned distribution laterals qty 8280 | ~3–4× too high | ~2000–2500 m total laterals | wrong quantity (per-container or reel length error) | PASS
— ¦ qty 4200 ¦ unit £20.8 | Drain/return risers qty 4200 | ~3× too high | ~1400 m total risers | wrong quantity (per-container multiplier) | PASS
C59, C05, C03, C60, C09, C34, C06, C07, C39, C63, C62, C41, C20, C10, C15, C11, C25, C26, C33, C18, C32, C30, C21, C24, C08, C36, C13, C04, C28, C58, C02, C23, C01, C35, C16, C37, C29, C38, C64, C12, C17, C31, C19, C40 (all water connections) | Each 'water connection' line priced £400–£3161 | 10–30× too high per connection | £50–£150 per connection (pipe spool + fittings) | wrong unit price (equipment or skid price copied into connection items) | PASS
TK-106, TK-108, TK-114, TK-103, TK-102, TK-101 | No raw-water tank, no dedicated RO permeate tank, no irrigation buffer tank | missing 3 tanks (~80–100 m³ total) | add 2–3 large tanks (raw + permeate + blend) to reach 120 m³ | missing component (only drain/fresh/nutrient/CIP tanks present) | PASS
— (no secondary containment line) | No bunding/containment for chemical storage or tank farm | absent | add civil bunding line (~£30–50k) | missing component | PASS
G-201 | Standby diesel generator present | not in benchmark scope | remove or move to separate capex | extra scope item | PASS
LLM-expected bill structure (top-down — what the cost SHOULD break into)
Expected line / category | % of cost | Note |  |  | Cell check
Piping & distribution (PVC/HDPE, fittings, manifolds) | 16% | Always underestimated; 200 valve zones = extensive pipe runs |  |  | PASS
RO system (membranes, HP pumps, housings, pre-treatment) | 14% | 8 m³/h skid with 75% recovery |  |  | PASS
Actuated valves + valve manifolds (200 count) | 12% | 200 motorised valves + associated manifolds and solenoids |  |  | PASS
PLC/SCADA/instrumentation (sensors, controls, panels) | 12% | 200 zones of control is significant I/O |  |  | PASS
Installation & commissioning labour | 11% | Mechanical + electrical + programming |  |  | PASS
Fertigation/dosing system (nutrient dosing, mixing) | 10% | Multi-zone fertigation skid |  |  | PASS
Water storage tanks (120 m³) | 8% | Poly/GRP tanks, permeate + raw + blend |  |  | PASS
Pumps (transfer, irrigation, booster) | 7% | Multiple duty/standby sets |  |  | PASS
Filtration (pre/post, UV disinfection) | 5% | Cartridge, media, UV for 45 m³/h |  |  | PASS
Civil/structural (tank pads, supports, containment) | 5% | Bund for 120 m³ storage |  |  | PASS
LLM reasoning (how the top-down expectation was formed)
A 6000-container cultivation facility with 200 actuated valve zones is a mid-to-large commercial fertigation build — the cost is dominated by the sheer extent of piping and valve manifold work, not the RO skid itself. The 8 m³/h RO is modest relative to the 45 m³/h irrigation demand, meaning storage buffering and blending strategy are critical. The £1.4M ceiling is achievable but tight; the system will live or die on piping/valve installation discipline and control system integration, which together account for ~40% of cost.

## ⚠ Checks
⚠ Computational checks — live invariants (== the CLI verifier) | [6 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · fail-count formula: 10 if 0 FAIL else max(0, 8 − 2 × fails) — deterministic invariants pass 7/7; cell completeness+type contract 197/197 · score = min over checks of 10 … · full audit: Quality & Audit tab
EXACTLY the checks scripts/deterministic-checks.py reports, rendered as LIVE Excel formulas over the data cells (cols J+). Edit a data cell and STATUS recomputes. RED = the engine's numbers do not reconcile.
Check | ACTUAL | EXPECTED | Δ (actual-exp) | Tol | STATUS | Detail / why | Cell check |  | DATA (live inputs — editable) |  |  |  | AGGREGATE DATA — one row per collapsed per-line invariant (P=line · Q=per-unit/actual £ · R=expected £ · S=qty · T=live mismatch flag). Edit Q/R/S and the aggregate row recomputes.
E1 · CONSISTENCY — per-unit×count, Σsub==line, rating==quantity | [12 empty] | BoM X-105: unit_gbp x qty == line_gbp | 672 | 672 | 1 | 0
All 190 BoM lines: unit £ × qty == line £ (aggregate — mismatching lines list individually) | 0 | 0 | 0 | 0 | PASS | 190 per-line invariants collapsed — each line lives in the DATA block (cols P–T, rows 5–194) with a LIVE mismatch flag at its own tolerance; ACTUAL = the number of mismatching lines. 0 exception(s) below. | PASS |  | All 190 BoM lines: unit £ × qty == line £ (aggregate — mismatching lines list individually) |  | 0 |  | BoM X-106: unit_gbp x qty == line_gbp | 283 | 283 | 1 | 0
All 17 BoM lines: Σ sub-component £ == line £ (aggregate — mismatching lines list individually) | 0 | 0 | 0 | 0 | PASS | 17 per-line invariants collapsed — each line lives in the DATA block (cols P–T, rows 195–211) with a LIVE mismatch flag at its own tolerance; ACTUAL = the number of mismatching lines. 0 exception(s) below. | PASS |  | All 17 BoM lines: Σ sub-component £ == line £ (aggregate — mismatching lines list individually) |  | 0 |  | BoM X-107: unit_gbp x qty == line_gbp | 183 | 183 | 1 | 0
BoM V-102: emitted kW rating == uv_disinfection_power_kw | 4 | 4.1 | -0.1 | 0.5 | PASS | V-102 requirement states 4 kW; contract uv_disinfection_power_kw = 4.1 kW. They must agree. | PASS |  | BoM V-102: emitted kW rating == uv_disinfection_power_kw | 4 | 4.1 |  | BoM X-108: unit_gbp x qty == line_gbp | 2 | 2 | 1 | 0
BoM P-106: emitted kW rating == fertigation_dosing_pump_power_kw | 8 | 7.5 | 0.5 | 0.75 | PASS | P-106 requirement states 8 kW; contract fertigation_dosing_pump_power_kw = 7.5 kW. They must agree. | PASS |  | BoM P-106: emitted kW rating == fertigation_dosing_pump_power_kw | 8 | 7.5 |  | BoM D-101: unit_gbp x qty == line_gbp | 148 | 148 | 1 | 0
BoM P-104: emitted kW rating == drain_transfer_pump_power_kw | 2 | 1.923 | 0.077 | 0.5 | PASS | P-104 requirement states 2 kW; contract drain_transfer_pump_power_kw = 1.923 kW. They must agree. | PASS |  | BoM P-104: emitted kW rating == drain_transfer_pump_power_kw | 2 | 1.923 |  | BoM X-109: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
BoM P-101: emitted kW rating == ro_high_pressure_pump_power_kw | 4 | 4.2 | -0.2 | 0.5 | PASS | P-101 requirement states 4 kW; contract ro_high_pressure_pump_power_kw = 4.2 kW. They must agree. | PASS |  | BoM P-101: emitted kW rating == ro_high_pressure_pump_power_kw | 4 | 4.2 |  | BoM G-201: unit_gbp x qty == line_gbp | 19200 | 19200 | 1 | 0
modules: every described sub-module carries components (no hollow module) | 0 | 0 | 0 | 0 | PASS | every sub-module that describes components backs its prose with ≥1 component word | PASS |  | modules: every described sub-module carries components (no hollow module) | 0 | 0 |  | BoM U-201: unit_gbp x qty == line_gbp | 4000 | 4000 | 1 | 0
[13 empty] | BoM EP-103: unit_gbp x qty == line_gbp | 62650 | 62650 | 1 | 0
E2 · ADEQUACY — rating ≥ duty (motor, breaker, cable, vessel, chiller) | [12 empty] | BoM EP-104: unit_gbp x qty == line_gbp | 3000 | 3000 | 1 | 0
Main incomer kVA >= connected load x 1.25 | 75 | 66.25 | 8.75 | 0 | PASS | Incomer 75 kVA (total_supply_demand_kva) must be >= 53 kW x 1.25 = 66.25 kVA (kVA >= kW for any power factor); magnitude sanity ceiling <= connected load 53 kW x 100 = 5300 (an absurdly-large rating must FAIL, not pass as 'adequate'). |  |  | Main incomer kVA >= connected load x 1.25 | 75 | 66.25 |  | BoM INV-1: unit_gbp x qty == line_gbp | 1086 | 1086 | 1 | 0
Cable CSA >= ampacity: Standby Diesel Generator | 1.5 | 1.5 | 0 | 0 | PASS | Mains Incomer->Standby Diesel Generator: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Standby Diesel Generator | 1.5 | 1.5 |  | BoM X-110: unit_gbp x qty == line_gbp | 283 | 283 | 1 | 0
Cable CSA >= ampacity: Transformer | 1.5 | 1.5 | 0 | 0 | PASS | Standby Diesel Gen->Transformer: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Transformer | 1.5 | 1.5 |  | BoM X-111: unit_gbp x qty == line_gbp | 2 | 2 | 1 | 0
Cable CSA >= ampacity: Main Switchboard | 1.5 | 1.5 | 0 | 0 | PASS | Transformer->Main Switchboard: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Main Switchboard | 1.5 | 1.5 |  | BoM INV-2: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
Cable CSA >= ampacity: Motor Control Center | 1.5 | 1.5 | 0 | 0 | PASS | Main Switchboard->Motor Control Center: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Motor Control Center | 1.5 | 1.5 |  | BoM F-1: unit_gbp x qty == line_gbp | 9100 | 9100 | 1 | 0
Cable CSA >= ampacity: 3 Phase Power Input | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->3 Phase Power Input: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: 3 Phase Power Input | 1.5 | 1.5 |  | BoM X-102: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
Cable CSA >= ampacity: Piping Network | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Piping Network: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Piping Network | 1.5 | 1.5 |  | BoM X-112: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
Cable CSA >= ampacity: Uv Disinfection | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Uv Disinfection: 8.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Uv Disinfection | 1.5 | 1.5 |  | BoM X-113: unit_gbp x qty == line_gbp | 1 | 1 | 1 | 0
Cable CSA >= ampacity: Fertigation Dosing Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Fertigation Dosing Pump: 15 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Fertigation Dosing Pump | 1.5 | 1.5 |  | BoM V-102: unit_gbp x qty == line_gbp | 17540 | 17540 | 1 | 0
Cable CSA >= ampacity: Hand Watering Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Hand Watering Pump: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Hand Watering Pump | 1.5 | 1.5 |  | BoM V-106: unit_gbp x qty == line_gbp | 8000 | 16000 | 2 | 0
Cable CSA >= ampacity: Drain Transfer Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Drain Transfer Pump: 3.9 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Drain Transfer Pump | 1.5 | 1.5 |  | BoM P-106: unit_gbp x qty == line_gbp | 8634 | 17268 | 2 | 0
Cable CSA >= ampacity: Cloth Filter | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Cloth Filter: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Cloth Filter | 1.5 | 1.5 |  | BoM TK-103: unit_gbp x qty == line_gbp | 2844 | 22752 | 8 | 0
Cable CSA >= ampacity: Irrigation Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Irrigation Pump: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Irrigation Pump | 1.5 | 1.5 |  | BoM P-102: unit_gbp x qty == line_gbp | 2500 | 2500 | 1 | 0
Cable CSA >= ampacity: Ro High Pressure Pump | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Ro High Pressure Pump: 8.4 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Ro High Pressure Pump | 1.5 | 1.5 |  | BoM TK-114: unit_gbp x qty == line_gbp | 4683 | 9366 | 2 | 0
Cable CSA >= ampacity: Gac Filter | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Gac Filter: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Gac Filter | 1.5 | 1.5 |  | BoM P-104: unit_gbp x qty == line_gbp | 1850 | 3700 | 2 | 0
Cable CSA >= ampacity: Permeate Outlet | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Permeate Outlet: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Permeate Outlet | 1.5 | 1.5 |  | BoM V-103: unit_gbp x qty == line_gbp | 8270 | 16540 | 2 | 0
Cable CSA >= ampacity: Concentrate Outlet | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Concentrate Outlet: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Concentrate Outlet | 1.5 | 1.5 |  | BoM V-105: unit_gbp x qty == line_gbp | 14825 | 14825 | 1 | 0
Cable CSA >= ampacity: Electrical Control Panel | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Electrical Control Panel: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Electrical Control Panel | 1.5 | 1.5 |  | BoM P-103: unit_gbp x qty == line_gbp | 9413 | 9413 | 1 | 0
Cable CSA >= ampacity: Control + Instrument UPS | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Control + Instrument UPS: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Control + Instrument UPS | 1.5 | 1.5 |  | BoM M-101: unit_gbp x qty == line_gbp | 1725 | 3450 | 2 | 0
Cable CSA >= ampacity: SCADA / Plant Control Sy | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->SCADA / Plant Control Sy: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: SCADA / Plant Control Sy | 1.5 | 1.5 |  | BoM Z-101: unit_gbp x qty == line_gbp | 8737 | 8737 | 1 | 0
Cable CSA >= ampacity: Electrical Control Cabin | 1.5 | 1.5 | 0 | 0 | PASS | Motor Control Cent->Electrical Control Cabin: 4.2 A needs >= 1.5 mm2 copper (air-rated ladder); chosen 1.5 mm2. |  |  | Cable CSA >= ampacity: Electrical Control Cabin | 1.5 | 1.5 |  | BoM P-101: unit_gbp x qty == line_gbp | 3850 | 3850 | 1 | 0
[13 empty] | BoM V-101: unit_gbp x qty == line_gbp | 14825 | 14825 | 1 | 0
E4 · COST — per-line price band & Σ lines == cover total | [12 empty] | BoM TK-108: unit_gbp x qty == line_gbp | 13615 | 13615 | 1 | 0
BoM X-105: unit price within x5 of distributor_price_gbp | 672 | 672.23 | -0.23 | 5 | PASS | X-105 (Rittal 1180.000): BoM unit £672 vs distributor_price_gbp £672 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-105: unit price within x5 of distributor_price_gbp | 672 | 672.23 |  | BoM TK-106: unit_gbp x qty == line_gbp | 13615 | 27230 | 2 | 0
BoM X-106: unit price within x5 of distributor_price_gbp | 283 | 283 | 0 | 5 | PASS | X-106 (ABB 1SDA067417R1): BoM unit £283 vs distributor_price_gbp £283 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-106: unit price within x5 of distributor_price_gbp | 283 | 283 |  | BoM X-114: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
BoM D-101: unit price within x5 of distributor_price_gbp | 148 | 148 | 0 | 5 | PASS | D-101 (TDK-Lambda DRB240-24-3-A0): BoM unit £148 vs distributor_price_gbp £148 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM D-101: unit price within x5 of distributor_price_gbp | 148 | 148 |  | BoM F-2: unit_gbp x qty == line_gbp | 9100 | 9100 | 1 | 0
BoM X-110: unit price within x5 of distributor_price_gbp | 283 | 283 | 0 | 5 | PASS | X-110 (ABB 1SDA067417R1): BoM unit £283 vs distributor_price_gbp £283 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-110: unit price within x5 of distributor_price_gbp | 283 | 283 |  | BoM X-115: unit_gbp x qty == line_gbp | 313 | 313 | 1 | 0
BoM V-102: unit price within x5 of price_estimate_gbp | 17540 | 12012 | 5528 | 5 | PASS | V-102 (WEDECO (Xylem) Spektron 30e): BoM unit £17,540 vs price_estimate_gbp £12,012 = x1.5. Flag when >x5 or <x0.2. |  |  | BoM V-102: unit price within x5 of price_estimate_gbp | 17540 | 12012 |  | BoM X-116: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM P-106: unit price within x5 of price_estimate_gbp | 8634 | 8634 | 0 | 5 | PASS | P-106 (Grundfos 96122012): BoM unit £8,634 vs price_estimate_gbp £8,634 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM P-106: unit price within x5 of price_estimate_gbp | 8634 | 8634 |  | BoM X-117: unit_gbp x qty == line_gbp | 160 | 160 | 1 | 0
BoM P-102: unit price within x5 of price_estimate_gbp | 2500 | 2500 | 0 | 5 | PASS | P-102 (Grundfos 96935501): price GROUNDED to the market band (£2,500); the pre-grounding price_estimate_gbp £7,796 was rejected as out-of-band — banding against it is not meaningful. |  |  | BoM P-102: unit price within x5 of price_estimate_gbp | 2500 | 2500 |  | BoM X-118: unit_gbp x qty == line_gbp | 132 | 132 | 1 | 0
BoM P-103: unit price within x5 of price_estimate_gbp | 9413 | 9413 | 0 | 5 | PASS | P-103 (Grundfos 96539165): BoM unit £9,413 vs price_estimate_gbp £9,413 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM P-103: unit price within x5 of price_estimate_gbp | 9413 | 9413 |  | BoM X-119: unit_gbp x qty == line_gbp | 985 | 985 | 1 | 0
BoM X-115: unit price within x5 of distributor_price_gbp | 313 | 313 | 0 | 5 | PASS | X-115 (Siemens 6ES7212-1AE40-0XB0): BoM unit £313 vs distributor_price_gbp £313 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-115: unit price within x5 of distributor_price_gbp | 313 | 313 |  | BoM X-120: unit_gbp x qty == line_gbp | 12 | 12 | 1 | 0
BoM X-117: unit price within x5 of distributor_price_gbp | 160 | 160 | 0 | 5 | PASS | X-117 (Siemens 6ES7241-1CH32-0XB0): BoM unit £160 vs distributor_price_gbp £160 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-117: unit price within x5 of distributor_price_gbp | 160 | 160 |  | BoM X-121: unit_gbp x qty == line_gbp | 595 | 595 | 1 | 0
BoM X-119: unit price within x5 of distributor_price_gbp | 985 | 985.41 | -0.41 | 5 | PASS | X-119 (HMS Networks (Ewon) FLEXY20500_00MA): BoM unit £985 vs distributor_price_gbp £985 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-119: unit price within x5 of distributor_price_gbp | 985 | 985.41 |  | BoM X-122: unit_gbp x qty == line_gbp | 313 | 313 | 1 | 0
BoM X-121: unit price within x5 of distributor_price_gbp | 595 | 595.03 | -0.03 | 5 | PASS | X-121 (Panasonic Industrial Automation AWHS1R070): BoM unit £595 vs distributor_price_gbp £595 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-121: unit price within x5 of distributor_price_gbp | 595 | 595.03 |  | BoM X-123: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
BoM X-122: unit price within x5 of distributor_price_gbp | 313 | 313 | 0 | 5 | PASS | X-122 (Siemens 6ES7212-1AE40-0XB0): BoM unit £313 vs distributor_price_gbp £313 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-122: unit price within x5 of distributor_price_gbp | 313 | 313 |  | BoM X-124: unit_gbp x qty == line_gbp | 500 | 500 | 1 | 0
BoM X-124: unit price within x5 of distributor_price_gbp | 500 | 985.41 | -485.41 | 5 | PASS | X-124 (HMS Networks (Ewon) FLEXY20500_00MA): BoM unit £500 vs distributor_price_gbp £985 = x0.5. Flag when >x5 or <x0.2. |  |  | BoM X-124: unit price within x5 of distributor_price_gbp | 500 | 985.41 |  | BoM I-103: unit_gbp x qty == line_gbp | 800 | 800 | 1 | 0
BoM X-125: unit price within x5 of distributor_price_gbp | 424 | 424.3 | -0.3 | 5 | PASS | X-125 (Sensata Technologies, Inc. SOL7A4): BoM unit £424 vs distributor_price_gbp £424 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-125: unit price within x5 of distributor_price_gbp | 424 | 424.3 |  | BoM X-125: unit_gbp x qty == line_gbp | 424 | 424 | 1 | 0
BoM X-128: unit price within x5 of price_estimate_gbp | 18 | 18 | 0 | 5 | PASS | X-128 (Pentair Fleck 2900S): BoM unit £18 vs price_estimate_gbp £18 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-128: unit price within x5 of price_estimate_gbp | 18 | 18 |  | BoM X-126: unit_gbp x qty == line_gbp | 200 | 40000 | 200 | 0
BoM V-107: unit price within x5 of distributor_price_gbp | 424 | 424.3 | -0.3 | 5 | PASS | V-107 (Sensata Technologies, Inc. SOL7A4): BoM unit £424 vs distributor_price_gbp £424 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM V-107: unit price within x5 of distributor_price_gbp | 424 | 424.3 |  | BoM X-127: unit_gbp x qty == line_gbp | 95 | 95 | 1 | 0
BoM I-108: unit price within x5 of price_estimate_gbp | 280 | 280 | 0 | 5 | PASS | I-108 (Hach 5500sc): BoM unit £280 vs price_estimate_gbp £280 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-108: unit price within x5 of price_estimate_gbp | 280 | 280 |  | BoM X-128: unit_gbp x qty == line_gbp | 18 | 18 | 1 | 0
BoM X-133: unit price within x5 of distributor_price_gbp | 250 | 250.34 | -0.34 | 5 | PASS | X-133 (Phoenix Contact 2838199): BoM unit £250 vs distributor_price_gbp £250 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-133: unit price within x5 of distributor_price_gbp | 250 | 250.34 |  | BoM FCV-201–202: unit_gbp x qty == line_gbp | 3312 | 6624 | 2 | 0
BoM I-111: unit price within x5 of own catalogue quote (engine-B corpus) | 76 | 75.75 | 0.25 | 5 | PASS | I-111 (Danfoss 060-121966): BoM unit £76 vs own catalogue quote (engine-B corpus) £76 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM I-111: unit price within x5 of own catalogue quote (engine-B corpus) | 76 | 75.75 |  | BoM V-107: unit_gbp x qty == line_gbp | 424 | 424 | 1 | 0
BoM X-141: unit price within x5 of price_estimate_gbp | 40 | 35 | 5 | 5 | PASS | X-141 (Eaton 216516): BoM unit £40 vs price_estimate_gbp £35 = x1.1. Flag when >x5 or <x0.2. |  |  | BoM X-141: unit price within x5 of price_estimate_gbp | 40 | 35 |  | BoM V-108: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
BoM X-142: unit price within x5 of price_estimate_gbp | 45 | 45 | 0 | 5 | PASS | X-142 (Legrand SRFL100G): BoM unit £45 vs price_estimate_gbp £45 = x1.0. Flag when >x5 or <x0.2. |  |  | BoM X-142: unit price within x5 of price_estimate_gbp | 45 | 45 |  | BoM V-109: unit_gbp x qty == line_gbp | 200 | 200 | 1 | 0
BoM X-145: unit price within x5 of distributor_price_gbp | 345 | 120.6 | 224.4 | 5 | PASS | X-145 (Siemens 3RU2126-4DB0): BoM unit £345 vs distributor_price_gbp £121 = x2.9. Flag when >x5 or <x0.2. |  |  | BoM X-145: unit price within x5 of distributor_price_gbp | 345 | 120.6 |  | BoM X-129: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
BoM I-114: unit price within x5 of price_estimate_gbp | 40 | 35 | 5 | 5 | PASS | I-114 (Eaton 216516): BoM unit £40 vs price_estimate_gbp £35 = x1.1. Flag when >x5 or <x0.2. |  |  | BoM I-114: unit price within x5 of price_estimate_gbp | 40 | 35 |  | BoM X-130: unit_gbp x qty == line_gbp | 200 | 200 | 1 | 0
Sigma requirementsBom.line_gbp == cover grand total | 808885 | 808885 | 0 | 8088.85 | PASS | Sum of 435 BoM line_gbp values vs parts-ledger.grand_total_gbp. |  |  | Sigma requirementsBom.line_gbp == cover grand total | 808885 | 808885 |  | BoM I-104: unit_gbp x qty == line_gbp | 80 | 80 | 1 | 0
[13 empty] | BoM I-105: unit_gbp x qty == line_gbp | 152 | 152 | 1 | 0
E5 · CONNECTIVITY/SPEC — out-of-spec tally & velocity limit | [12 empty] | BoM I-106: unit_gbp x qty == line_gbp | 80 | 80 | 1 | 0
Process parts with both fluid in+out (coverage >= 80%) | 1 | 0.8 | 0.2 | 0 | PASS | 14 of 14 process parts are fully connected (fluid in AND out). The connection graph is incomplete below 80% — a vessel/pump/valve with a missing feed or discharge is a topology gap. 14 concern(s) total. |  |  | Process parts with both fluid in+out (coverage >= 80%) | 0.071429 | 0.8 | 14 | BoM I-107: unit_gbp x qty == line_gbp | 80 | 80 | 1 | 0
Instruments associated to what they measure (coverage >= 80%) | 1 | 0.8 | 0.2 | 0 | PASS | 14 of 14 instruments are wired (>=1 signal/sense association). Below 80% leaves orphan sensors not tied to the process or the control system. |  |  | Instruments associated to what they measure (coverage >= 80%) | 0.071429 | 0.8 | 14 | BoM LT-201–213: unit_gbp x qty == line_gbp | 900 | 11700 | 13 | 0
Ledger completeness: every part shows its required input + output | 0 | 0 | 0 | 0 | PASS | 0 part(s) are missing a required connection in the authored ledger — the design is not fully connected. Each process part must show a fluid INPUT and OUTPUT (naming what it connects to/from); a powered part a power feed; an instrument a signal tie. All parts fully connected. Fix at the ledger completion (close every part's missing direction), not by inventing a render pipe. |  |  | Ledger completeness: every part shows its required input + output | 0 | 0 |  | BoM LT-214: unit_gbp x qty == line_gbp | 900 | 900 | 1 | 0
Ledger referential integrity: every connection names a real part | 0 | 0 | 0 | 0 | PASS | 0 connection reference(s) point to a name that is not an authored part — the graph is not fully traceable. Every edge A→B must name B by its exact part name AND appear in B's inputs. All references resolve; the whole system is traceable part-to-part. |  |  | Ledger referential integrity: every connection names a real part | 0 | 0 |  | BoM LT-215–217: unit_gbp x qty == line_gbp | 900 | 2700 | 3 | 0
Connection rows within_spec == false (tally) | 0 | 0 | 0 | 0 | PASS | 0 of 74 connection runs are out of spec (e.g. over-velocity pipe / over-voltdrop cable). All within spec. |  |  | Connection rows within_spec == false (tally) | 0 | 0 |  | BoM AT-201: unit_gbp x qty == line_gbp | 1300 | 1300 | 1 | 0
Worst pipe velocity <= spec limit (DN80) | 1.457 | 3 | -1.543 | 0 | PASS | DN80 carries 1.457 m/s vs its stated limit 3 m/s. Over-velocity = erosion / head loss (0 pipe specs over limit). |  |  | Worst pipe velocity <= spec limit (DN80) | 1.457 | 3 |  | BoM PT-201–217: unit_gbp x qty == line_gbp | 700 | 11900 | 17 | 0
Longest connection run <= plant diagonal x 1.8 (length plausibility) | 35.9 | 54.4 | -18.5 | 0 | PASS | Longest routed run 36 m (Permeate Outlet -> Cip Tank) vs plant footprint diagonal 30 m. A run beyond ~1.8x the diagonal is not physical inside the plant envelope -> the layout is loose and its length x GBP/m cost is inflated. Fix at the placement source (cluster connected equipment), not the cost rate. |  |  | Longest connection run <= plant diagonal x 1.8 (length plausibility) | 35.9 | 54.4 |  | BoM I-108: unit_gbp x qty == line_gbp | 280 | 280 | 1 | 0
Total connection length <= diagonal x n_runs x 1.25 | 661 | 1814 | -1153 | 0 | PASS | Total routed connection length 661 m over 48 runs vs a plausible 1814 m (diagonal 30 m x 48 runs x 1.25). A systemic overshoot means the layout strings equipment wider than the building -> inflated pipe/cable take-off. |  |  | Total connection length <= diagonal x n_runs x 1.25 | 661 | 1814 |  | BoM I-109: unit_gbp x qty == line_gbp | 80 | 80 | 1 | 0
[13 empty] | BoM I-110: unit_gbp x qty == line_gbp | 30 | 30 | 1 | 0
E6 · BRIEF — design realises each stated brief target metric (±5%) | [12 empty] | BoM X-131: unit_gbp x qty == line_gbp | 152 | 152 | 1 | 0
Brief target met: water_storage_capacity_m3 | 120 | 120 | 0 | 6 | PASS | Brief target water_storage_capacity_m3 = 120 m3; design (water_storage_capacity_m3) = 120 m3 — the design must realise the brief target within ±5%. |  |  | Brief target met: water_storage_capacity_m3 | 120 | 120 |  | BoM EP-102: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
Brief target met: irrigation_demand_m3_per_hr | 90 | 45 | 45 | 2.25 | PASS | Brief target irrigation_demand_m3_per_hr = 45 m3/h; design (irrigation_demand_m3_h) = 90 m3/h — the design must realise the brief target within ±5%. |  |  | Brief target met: irrigation_demand_m3_per_hr | 90 | 45 |  | BoM EP-101: unit_gbp x qty == line_gbp | 3000 | 3000 | 1 | 0
Brief target met: ro_permeate_capacity_m3_per_hr | 8 | 8 | 0 | 0.4 | PASS | Brief target ro_permeate_capacity_m3_per_hr = 8 m3/h; design (ro_permeate_capacity_m3_h) = 8 m3/h — the design must realise the brief target within ±5%. |  |  | Brief target met: ro_permeate_capacity_m3_per_hr | 8 | 8 |  | BoM X-132: unit_gbp x qty == line_gbp | 218 | 218 | 1 | 0
Brief target met: hand_watering_capacity_m3_per_hr | 25 | 25 | 0 | 1.25 | PASS | Brief target hand_watering_capacity_m3_per_hr = 25 m3/h; design (hand_watering_pump_throughput_m3_h) = 25 m3/h — the design must realise the brief target within ±5%. |  |  | Brief target met: hand_watering_capacity_m3_per_hr | 25 | 25 |  | BoM X-133: unit_gbp x qty == line_gbp | 250 | 250 | 1 | 0
Brief target met: ro_recovery_percent | 75 | 75 | 0 | 3.75 | PASS | Brief target ro_recovery_percent = 75 %; design (ro_recovery_percent) = 75 % — the design must realise the brief target within ±5%. |  |  | Brief target met: ro_recovery_percent | 75 | 75 |  | BoM X-104: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
[13 empty] | BoM X-103: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
E7 · PROVENANCE — every engineering-tool output is actually USED by the design (no stale/orphaned tool computations) | [12 empty] | BoM X-134: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
Tool output used: incident_energy_cal_cm2 | 0.741 | 0.741 | 0 | 0.015 | PASS | arc-flash:ieee-1584 incident_energy_cal_cm2=0.741 matches contract incident_energy_cal_cm2. |  |  | Tool output used: incident_energy_cal_cm2 | 0.741 | 0.741 |  | BoM X-135: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
Tool output used: ph_control_kp | 0.296 | 0.296 | 0 | 0.01 | PASS | control-systems:pid-tuning ph_control_kp=0.296464 matches contract ph_control_kp. |  |  | Tool output used: ph_control_kp | 0.296 | 0.296 |  | BoM X-136: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
Tool output used: main_feeder_cable_csa_mm2 | 25 | 25 | 0 | 0.5 | PASS | electrical:cable-sizing main_feeder_cable_csa_mm2=25 matches contract main_feeder_cable_csa_mm2. |  |  | Tool output used: main_feeder_cable_csa_mm2 | 25 | 25 |  | BoM X-137: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
Tool output used: cable_voltdrop_pct | 2.03 | 2.03 | 0 | 0.041 | PASS | electrical:cable-sizing cable_voltdrop_pct=2.03 matches contract cable_voltdrop_pct. |  |  | Tool output used: cable_voltdrop_pct | 2.03 | 2.03 |  | BoM TX-101: unit_gbp x qty == line_gbp | 3000 | 3000 | 1 | 0
Tool output used: transformer_kva | 75 | 75 | 0 | 1.5 | PASS | electrical:transformer-sizing transformer_kva=75 matches contract transformer_kva. |  |  | Tool output used: transformer_kva | 75 | 75 |  | BoM X-138: unit_gbp x qty == line_gbp | 300 | 300 | 1 | 0
Tool output used: transformer_secondary_current_a | 108.25 | 108.25 | 0 | 2.165 | PASS | electrical:transformer-sizing transformer_secondary_current_a=108.25 matches contract transformer_secondary_current_a. |  |  | Tool output used: transformer_secondary_current_a | 108.25 | 108.25 |  | BoM X-139: unit_gbp x qty == line_gbp | 1 | 1 | 1 | 0
Tool output used: uv_disinfection_throughput_m3_h | 90 | 90 | 0 | 1.8 | PASS | first-principles:disinfection uv_disinfection_throughput_m3_h=90 matches contract uv_disinfection_throughput_m3_h. |  |  | Tool output used: uv_disinfection_throughput_m3_h | 90 | 90 |  | BoM X-140: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
Tool output used: uv_disinfection_power_kw | 4.1 | 4.1 | 0 | 0.082 | PASS | first-principles:disinfection uv_disinfection_power_kw=4.1 matches contract uv_disinfection_power_kw. |  |  | Tool output used: uv_disinfection_power_kw | 4.1 | 4.1 |  | BoM F-3: unit_gbp x qty == line_gbp | 11000 | 11000 | 1 | 0
Tool output used: uv_disinfection_count | 1 | 1 | 0 | 0.02 | PASS | first-principles:disinfection uv_disinfection_count=1 matches contract uv_disinfection_count. |  |  | Tool output used: uv_disinfection_count | 1 | 1 |  | BoM V-110: unit_gbp x qty == line_gbp | 18 | 18 | 1 | 0
Tool output used: connected_electrical_load_kw | 53 | 53 | 0 | 1.06 | PASS | first-principles:electrical connected_electrical_load_kw=53 matches contract connected_electrical_load_kw. |  |  | Tool output used: connected_electrical_load_kw | 53 | 53 |  | BoM I-111: unit_gbp x qty == line_gbp | 76 | 76 | 1 | 0
Tool output used: irrigation_demand_m3_h | 90 | 90 | 0 | 1.8 | PASS | first-principles:process irrigation_demand_m3_h=90 matches contract irrigation_demand_m3_h. |  |  | Tool output used: irrigation_demand_m3_h | 90 | 90 |  | BoM I-112: unit_gbp x qty == line_gbp | 30 | 30 | 1 | 0
Tool output used: water_storage_capacity_m3 | 120 | 120 | 0 | 2.4 | PASS | first-principles:process water_storage_capacity_m3=120 matches contract water_storage_capacity_m3. |  |  | Tool output used: water_storage_capacity_m3 | 120 | 120 |  | BoM X-141: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
Tool output used: softener_vessel_volume_each_m3 | 1.5 | 1.5 | 0 | 0.03 | PASS | first-principles:process softener_vessel_volume_each_m3=1.5 matches contract softener_vessel_volume_each_m3. |  |  | Tool output used: softener_vessel_volume_each_m3 | 1.5 | 1.5 |  | BoM I-102: unit_gbp x qty == line_gbp | 8023 | 8023 | 1 | 0
Tool output used: fertigation_dosing_capacity_m3_per_hr | 90 | 90 | 0 | 1.8 | PASS | first-principles:process fertigation_dosing_capacity_m3_per_hr=90 matches contract fertigation_dosing_capacity_m3_per_hr. |  |  | Tool output used: fertigation_dosing_capacity_m3_per_hr | 90 | 90 |  | BoM X-142: unit_gbp x qty == line_gbp | 45 | 45 | 1 | 0
Tool output used: total_supply_demand_kw | 53 | 53 | 0 | 1.06 | PASS | first-principles:process total_supply_demand_kw=53 matches contract total_supply_demand_kw. |  |  | Tool output used: total_supply_demand_kw | 53 | 53 |  | BoM X-143: unit_gbp x qty == line_gbp | 3 | 3 | 1 | 0
Tool output used: main_incomer_breaker_a | 106 | 106 | 0 | 2.12 | PASS | first-principles:process main_incomer_breaker_a=106 matches contract main_incomer_breaker_a. |  |  | Tool output used: main_incomer_breaker_a | 106 | 106 |  | BoM X-144: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
Tool output used: main_incomer_breaker_frame_a | 125 | 125 | 0 | 2.5 | PASS | first-principles:process main_incomer_breaker_frame_a=125 matches contract main_incomer_breaker_frame_a. |  |  | Tool output used: main_incomer_breaker_frame_a | 125 | 125 |  | BoM I-113: unit_gbp x qty == line_gbp | 30 | 30 | 1 | 0
Tool output used: gac_filter_vessel_volume_m3 | 1.8 | 1.8 | 0 | 0.036 | PASS | first-principles:solids gac_filter_vessel_volume_m3=1.8 matches contract gac_filter_vessel_volume_m3. |  |  | Tool output used: gac_filter_vessel_volume_m3 | 1.8 | 1.8 |  | BoM V-111: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
Tool output used: gac_vessel_diameter_m | 1.359 | 1.359 | 0 | 0.027 | PASS | gac-filter:liquid-phase-sizing gac_vessel_diameter_m=1.35875 matches contract gac_vessel_diameter_m. |  |  | Tool output used: gac_vessel_diameter_m | 1.359 | 1.359 |  | BoM X-145: unit_gbp x qty == line_gbp | 345 | 345 | 1 | 0
Tool output used: softener_salt_consumption_max_kg_per_regen | 46.199 | 46.199 | 0 | 0.924 | PASS | ion-exchange:softener-sizing softener_salt_consumption_max_kg_per_regen=46.1993 matches contract softener_salt_consumption_max_kg_per_regen. |  |  | Tool output used: softener_salt_consumption_max_kg_per_regen | 46.199 | 46.199 |  | BoM I-114: unit_gbp x qty == line_gbp | 40 | 40 | 1 | 0
Tool output used: drain_collection_sump_volume_each_m3 | 5 | 5 | 0 | 0.1 | PASS | irrigation:ebb-flow-demand drain_collection_sump_volume_each_m3=5 matches contract drain_collection_sump_volume_each_m3. |  |  | Tool output used: drain_collection_sump_volume_each_m3 | 5 | 5 |  | BoM X-146: unit_gbp x qty == line_gbp | 72 | 72 | 1 | 0
Tool output used: irrigation_pump_motor_kw | 9.653 | 9.653 | 0 | 0.193 | PASS | irrigation:pump-sizing irrigation_pump_motor_kw=9.653 matches contract irrigation_pump_motor_kw. |  |  | Tool output used: irrigation_pump_motor_kw | 9.653 | 9.653 |  | BoM X-147: unit_gbp x qty == line_gbp | 9 | 9 | 1 | 0
Tool output used: irrigation_pump_flow_m3_h | 90 | 90 | 0 | 1.8 | PASS | irrigation:pump-sizing irrigation_pump_flow_m3_h=90 matches contract irrigation_pump_flow_m3_h. |  |  | Tool output used: irrigation_pump_flow_m3_h | 90 | 90 |  | BoM X-148: unit_gbp x qty == line_gbp | 15 | 15 | 1 | 0
Tool output used: total_system_mass_kg | 1500.8 | 1500.8 | 0 | 30.016 | PASS | mass-aggregator:envelope-check total_system_mass_kg=1500.8 matches contract total_system_mass_kg. |  |  | Tool output used: total_system_mass_kg | 1500.8 | 1500.8 |  | BoM X-149: unit_gbp x qty == line_gbp | 2 | 2 | 1 | 0
Tool output used: cloth_filter_area_m2 | 3.466 | 3.466 | 0 | 0.069 | PASS | mechanical-filtration:cloth-screen cloth_filter_area_m2=3.46572 matches contract cloth_filter_area_m2. |  |  | Tool output used: cloth_filter_area_m2 | 3.466 | 3.466 |  | BoM X-101: unit_gbp x qty == line_gbp | 218 | 218 | 1 | 0
Tool output used: filter_hydraulic_loading_m_h | 23.083 | 23.083 | 0 | 0.462 | PASS | mechanical-filtration:cloth-screen filter_hydraulic_loading_m_h=23.0832 matches contract filter_hydraulic_loading_m_h. |  |  | Tool output used: filter_hydraulic_loading_m_h | 23.083 | 23.083 |  | BoM TK-102: unit_gbp x qty == line_gbp | 4000 | 4000 | 1 | 0
Tool output used: acid_dose_rate_ml_min | 640 | 640 | 0 | 12.8 | PASS | ph-titration:sizing acid_dose_rate_ml_min=640 matches contract acid_dose_rate_ml_min. |  |  | Tool output used: acid_dose_rate_ml_min | 640 | 640 |  | BoM X-150: unit_gbp x qty == line_gbp | 95 | 95 | 1 | 0
Tool output used: gac_vessel_mass_kg | 600.811 | 600.811 | 0 | 12.016 | PASS | pressure-vessel:design gac_vessel_mass_kg=600.811 matches contract gac_vessel_mass_kg. |  |  | Tool output used: gac_vessel_mass_kg | 600.811 | 600.811 |  | BoM TK-101: unit_gbp x qty == line_gbp | 4000 | 4000 | 1 | 0
Tool output used: softener_vessel_mass_kg | 556.127 | 556.127 | 0 | 11.123 | PASS | pressure-vessel:design softener_vessel_mass_kg=556.127 matches contract softener_vessel_mass_kg. |  |  | Tool output used: softener_vessel_mass_kg | 556.127 | 556.127 |  | BoM C01: unit_gbp x qty == line_gbp | 905 | 905 | 1 | 0
Tool output used: fertigation_dosing_pump_power_kw | 7.5 | 7.5 | 0 | 0.15 | PASS | process:pump-sizing fertigation_dosing_pump_power_kw=7.5 matches contract fertigation_dosing_pump_power_kw. |  |  | Tool output used: fertigation_dosing_pump_power_kw | 7.5 | 7.5 |  | BoM C02: unit_gbp x qty == line_gbp | 911 | 911 | 1 | 0
Tool output used: drain_transfer_pump_power_kw | 1.923 | 1.923 | 0 | 0.038 | PASS | process:pump-sizing drain_transfer_pump_power_kw=1.923 matches contract drain_transfer_pump_power_kw. |  |  | Tool output used: drain_transfer_pump_power_kw | 1.923 | 1.923 |  | BoM C03: unit_gbp x qty == line_gbp | 1614 | 1614 | 1 | 0
Tool output used: fresh_water_storage_capacity_m3 | 40 | 40 | 0 | 0.8 | PASS | water-storage:buffer-sizing fresh_water_storage_capacity_m3=40 matches contract fresh_water_storage_capacity_m3. |  |  | Tool output used: fresh_water_storage_capacity_m3 | 40 | 40 |  | BoM C04: unit_gbp x qty == line_gbp | 975 | 975 | 1 | 0
Tool output used: drain_water_tank_volume_each_m3 | 40 | 40 | 0 | 0.8 | PASS | water-storage:buffer-sizing drain_water_tank_volume_each_m3=40 matches contract drain_water_tank_volume_each_m3. |  |  | Tool output used: drain_water_tank_volume_each_m3 | 40 | 40 |  | BoM C05: unit_gbp x qty == line_gbp | 2232 | 2232 | 1 | 0
Tool output used: total_water_storage_volume_m3 | 261.6 | 261.6 | 0 | 5.232 | PASS | water-storage:buffer-sizing total_water_storage_volume_m3=261.6 matches contract total_water_storage_volume_m3. |  |  | Tool output used: total_water_storage_volume_m3 | 261.6 | 261.6 |  | BoM C06: unit_gbp x qty == line_gbp | 1443 | 1443 | 1 | 0
Tool output used: ro_membrane_area_m2 | 363.6 | 363.6 | 0 | 7.272 | PASS | water-treatment-ro:sizing ro_membrane_area_m2=363.6 matches contract ro_membrane_area_m2. |  |  | Tool output used: ro_membrane_area_m2 | 363.6 | 363.6 |  | BoM C07: unit_gbp x qty == line_gbp | 1419 | 1419 | 1 | 0
Tool output used: ro_permeate_production_m3_per_hr | 8 | 8 | 0 | 0.16 | PASS | water-treatment-ro:sizing ro_permeate_production_m3_per_hr=8 matches contract ro_permeate_production_m3_per_hr. |  |  | Tool output used: ro_permeate_production_m3_per_hr | 8 | 8 |  | BoM C08: unit_gbp x qty == line_gbp | 1023 | 1023 | 1 | 0
Tool output used: estimated_capex_gbp | 115727 | 115727 | 0 | 2314.54 | PASS | water-treatment-ro:sizing estimated_capex_gbp=115727 matches contract estimated_capex_gbp. |  |  | Tool output used: estimated_capex_gbp | 115727 | 115727 |  | BoM C09: unit_gbp x qty == line_gbp | 1559 | 1559 | 1 | 0
[13 empty] | BoM C10: unit_gbp x qty == line_gbp | 1243 | 1243 | 1 | 0
[13 empty] | BoM C11: unit_gbp x qty == line_gbp | 1176 | 1176 | 1 | 0
[13 empty] | BoM C12: unit_gbp x qty == line_gbp | 601 | 601 | 1 | 0
Brief compliance — every target vs achieved vs PASS/FAIL | [12 empty] | BoM C13: unit_gbp x qty == line_gbp | 984 | 984 | 1 | 0
[13 empty] | BoM C14: unit_gbp x qty == line_gbp | 500 | 500 | 1 | 0
Brief metric | Target | Unit | Matched contract quantity | Achieved | Direction | STATUS | Note | Cell check |  |  |  |  | BoM C15: unit_gbp x qty == line_gbp | 1236 | 1236 | 1 | 0
Cultivation containers count | 6000 | count | Cultivation container count | 6000 | ≥ target (meet/exceed) | PASS | brief key: cultivation_containers_count → contract: cultivation_container_count · unit family: count | PASS |  |  |  |  | BoM C16: unit_gbp x qty == line_gbp | 879 | 879 | 1 | 0
Water storage capacity m3 | 120 | m3 | Water storage capacity m3 | 120 | ≥ target (meet/exceed) | PASS | brief key: water_storage_capacity_m3 → contract: water_storage_capacity_m3 · unit family: volume_m3 | PASS |  |  |  |  | BoM C17: unit_gbp x qty == line_gbp | 516 | 516 | 1 | 0
Actuated valves count | 200 | count | Actuated distribution valve count | 200 | ≥ target (meet/exceed) | PASS | brief key: actuated_valves_count → contract: actuated_distribution_valve_count · unit family: count | PASS |  |  |  |  | BoM C18: unit_gbp x qty == line_gbp | 1138 | 1138 | 1 | 0
Irrigation demand (m³/h) | 45 | m3/h | Irrigation pump flow (m³/h) | 90 | ≥ target (meet/exceed) | PASS | brief key: irrigation_demand_m3_per_hr → contract: irrigation_pump_flow_m3_h · unit family: flow_m3h | PASS |  |  |  |  | BoM C19: unit_gbp x qty == line_gbp | 312 | 312 | 1 | 0
Ro permeate capacity (m³/h) | 8 | m3/h | Ro permeate capacity (m³/h) | 8 | ≥ target (meet/exceed) | PASS | brief key: ro_permeate_capacity_m3_per_hr → contract: ro_permeate_capacity_m3_h · unit family: flow_m3h | PASS |  |  |  |  | BoM C20: unit_gbp x qty == line_gbp | 1273 | 1273 | 1 | 0
Hand watering capacity (m³/h) | 25 | m3/h | Hand watering pump throughput (m³/h) | 25 | ≥ target (meet/exceed) | PASS | brief key: hand_watering_capacity_m3_per_hr → contract: hand_watering_pump_throughput_m3_h · unit family: flow_m3h | PASS |  |  |  |  | BoM C21: unit_gbp x qty == line_gbp | 1041 | 1041 | 1 | 0
Ro recovery (%) | 75 | % | Ro recovery (%) | 75 | ≥ target (meet/exceed) | PASS | brief key: ro_recovery_percent → contract: ro_recovery_percent | PASS |  |  |  |  | BoM C22: unit_gbp x qty == line_gbp | 487 | 487 | 1 | 0
[13 empty] | BoM C23: unit_gbp x qty == line_gbp | 909 | 909 | 1 | 0
Tool provenance — input → output traceability (USED / STALE / ORPHANED) | [12 empty] | BoM C24: unit_gbp x qty == line_gbp | 1039 | 1039 | 1 | 0
[13 empty] | BoM C25: unit_gbp x qty == line_gbp | 1169 | 1169 | 1 | 0
Tool | Output field | Value | Unit | Input — from | → Consumed by | Status | Cell check | [5 empty] | BoM C26: unit_gbp x qty == line_gbp | 1169 | 1169 | 1 | 0
arc-flash:ieee-1584 | incident_energy_cal_cm2 | 0.741 | cal/cm2 | inputs from: brief | incident_energy_cal_cm2 = 0.741 | USED | PASS | [5 empty] | BoM C27: unit_gbp x qty == line_gbp | 413 | 413 | 1 | 0
control-systems:pid-tuning | kp | 0.29646 |  | inputs from: brief | ph_control_kp = 0.296464 | USED | PASS | [5 empty] | BoM C28: unit_gbp x qty == line_gbp | 921 | 921 | 1 | 0
electrical:cable-sizing | main_feeder_cable_csa_mm2 | 25 | mm2 | inputs from: electrical:transformer-sizing + brief | main_feeder_cable_csa_mm2 = 25 | USED | PASS | [5 empty] | BoM C29: unit_gbp x qty == line_gbp | 678 | 678 | 1 | 0
electrical:cable-sizing | cable_voltdrop_pct | 2.03 | % | inputs from: electrical:transformer-sizing + brief | cable_voltdrop_pct = 2.03 | USED | PASS | [5 empty] | BoM C30: unit_gbp x qty == line_gbp | 1059 | 1059 | 1 | 0
electrical:transformer-sizing | transformer_kva | 75 | kVA | inputs from: brief | transformer_kva = 75 | USED | PASS | [5 empty] | BoM C31: unit_gbp x qty == line_gbp | 318 | 318 | 1 | 0
electrical:transformer-sizing | transformer_secondary_current_a | 108.25 | A | inputs from: brief | transformer_secondary_current_a = 108.25 | USED | PASS | [5 empty] | BoM C32: unit_gbp x qty == line_gbp | 1069 | 1069 | 1 | 0
first-principles:disinfection | uv_disinfection_throughput_m3_h | 90 | m³/h | medium-pressure UV-C reactor sized to the peak recirculated flow (= irrigation demand 90 m³/h) for Legionella control at ≈40 mJ/cm² | uv_disinfection_throughput_m3_h = 90 | USED | PASS | [5 empty] | BoM C33: unit_gbp x qty == line_gbp | 1158 | 1158 | 1 | 0
first-principles:disinfection | uv_disinfection_power_kw | 4.1 | kW | UV-C lamp electrical draw ≈ 0.045 kW per m³/h at the Legionella dose (90 m³/h × 0.045) | uv_disinfection_power_kw = 4.1 | USED | PASS | [5 empty] | BoM C34: unit_gbp x qty == line_gbp | 1493 | 1493 | 1 | 0
first-principles:disinfection | uv_disinfection_count | 1 | off | one duty UV-C reactor on the common recirculation main (all stored/recirculated water passes it before distribution) | uv_disinfection_count = 1 | USED | PASS | [5 empty] | BoM C35: unit_gbp x qty == line_gbp | 897 | 897 | 1 | 0
first-principles:electrical | connected_electrical_load_kw | 53 | kW | sum of pump + dosing + control loads ≈ 53 kW — a pumping/dosing plant, NOT a megawatt facility (lighting + HVAC are out of scope) | connected_electrical_load_kw = 53 | USED | PASS | [5 empty] | BoM C36: unit_gbp x qty == line_gbp | 1004 | 1004 | 1 | 0
first-principles:process | irrigation_demand_m3_h | 90 | m³/h | peak irrigation demand = 45 m³/h per department × 2 departments; lock-gate HARD slot (exit 22) | irrigation_demand_m3_h = 90 | USED | PASS | [5 empty] | BoM C37: unit_gbp x qty == line_gbp | 875 | 875 | 1 | 0
first-principles:process | water_storage_capacity_m3 | 120 | m³ | total water storage = 3 galvanised tanks (1 fresh + 2 drain) × 40 m³ = 120 m³ | water_storage_capacity_m3 = 120 | USED | PASS | [5 empty] | BoM C38: unit_gbp x qty == line_gbp | 625 | 625 | 1 | 0
first-principles:process | softener_vessel_volume_each_m3 | 1.5 | m³ | glass-fibre softener vessel (350 L resin each, 14 m³/h duplex) | softener_vessel_volume_each_m3 = 1.5 | USED | PASS | [5 empty] | BoM C39: unit_gbp x qty == line_gbp | 1384 | 1384 | 1 | 0
first-principles:process | fertigation_dosing_capacity_m3_per_hr | 90 | m³/h | total fertigation dosing capacity = 2 units × 45 m³/h = 90 m³/h | fertigation_dosing_capacity_m3_per_hr = 90 | USED | PASS | [5 empty] | BoM C40: unit_gbp x qty == line_gbp | 406 | 406 | 1 | 0
first-principles:process | total_supply_demand_kw | 53 | kW | total connected electrical demand of the water plant | total_supply_demand_kw = 53 | USED | PASS | [5 empty] | BoM C41: unit_gbp x qty == line_gbp | 1296 | 1296 | 1 | 0
first-principles:process | main_incomer_breaker_a | 106 | A | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_a = 106 | USED | PASS | [5 empty] | BoM C42: unit_gbp x qty == line_gbp | 43 | 43 | 1 | 0
first-principles:process | main_incomer_breaker_frame_a | 125 | A | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_frame_a = 125 | USED | PASS | [5 empty] | BoM C43: unit_gbp x qty == line_gbp | 37 | 37 | 1 | 0
first-principles:solids | gac_filter_vessel_volume_m3 | 1.8 | m³ | granular-activated-carbon filter vessel (1 × 42-inch tank, 14.5 m³/h) | gac_filter_vessel_volume_m3 = 1.8 | USED | PASS | [5 empty] | BoM C44: unit_gbp x qty == line_gbp | 30 | 30 | 1 | 0
gac-filter:liquid-phase-sizing | gac_vessel_diameter_m | 1.3587 | m | inputs from: brief | gac_vessel_diameter_m = 1.35875 | USED | PASS | [5 empty] | BoM C45: unit_gbp x qty == line_gbp | 72 | 72 | 1 | 0
ion-exchange:softener-sizing | softener_salt_consumption_max_kg_per_regen | 46.1993 | kg | inputs from: brief | softener_salt_consumption_max_kg_per_regen = 46.1993 | USED | PASS | [5 empty] | BoM C46: unit_gbp x qty == line_gbp | 29 | 29 | 1 | 0
irrigation:ebb-flow-demand | drain_collection_sump_volume_each_m3 | 5 | m3 | inputs from: brief | drain_collection_sump_volume_each_m3 = 5 | USED | PASS | [5 empty] | BoM C47: unit_gbp x qty == line_gbp | 90 | 90 | 1 | 0
irrigation:pump-sizing | motor_power_kw | 9.653 | kW | inputs from: irrigation:ebb-flow-demand + brief | irrigation_pump_motor_kw = 9.653 | USED | PASS | [5 empty] | BoM C48: unit_gbp x qty == line_gbp | 87 | 87 | 1 | 0
irrigation:pump-sizing | pump_flow_m3_h | 90 | m3/h | inputs from: irrigation:ebb-flow-demand + brief | irrigation_pump_flow_m3_h = 90 | USED | PASS | [5 empty] | BoM C49: unit_gbp x qty == line_gbp | 83 | 83 | 1 | 0
mass-aggregator:envelope-check | total_system_mass_kg | 1500.8 | kg | inputs from: irrigation:pump-sizing, pressure-vessel:design + brief | total_system_mass_kg = 1500.8 | USED | PASS | [5 empty] | BoM C50: unit_gbp x qty == line_gbp | 106 | 106 | 1 | 0
mechanical-filtration:cloth-screen | cloth_filter_area_m2 | 3.4657 | m2 | inputs from: brief | cloth_filter_area_m2 = 3.46572 | USED | PASS | [5 empty] | BoM C51: unit_gbp x qty == line_gbp | 94 | 94 | 1 | 0
mechanical-filtration:cloth-screen | filter_hydraulic_loading_m_h | 23.0832 | m/h | inputs from: brief | filter_hydraulic_loading_m_h = 23.0832 | USED | PASS | [5 empty] | BoM C52: unit_gbp x qty == line_gbp | 76 | 76 | 1 | 0
ph-titration:sizing | acid_dose_rate_ml_min | 640 | mL/min | inputs from: brief | acid_dose_rate_ml_min = 640 | USED | PASS | [5 empty] | BoM C53: unit_gbp x qty == line_gbp | 96 | 96 | 1 | 0
pressure-vessel:design | mass_kg | 600.811 | kg | inputs from: gac-filter:liquid-phase-sizing + brief | gac_vessel_mass_kg = 600.811 | USED | PASS | [5 empty] | BoM C54: unit_gbp x qty == line_gbp | 109 | 109 | 1 | 0
pressure-vessel:design | mass_kg | 556.127 | kg | inputs from: gac-filter:liquid-phase-sizing + brief | softener_vessel_mass_kg = 556.127 | USED | PASS | [5 empty] | BoM C55: unit_gbp x qty == line_gbp | 113 | 113 | 1 | 0
process:pump-sizing | motor_power_kw | 7.5 | kW | inputs from: brief | fertigation_dosing_pump_power_kw = 7.5 | USED | PASS | [5 empty] | BoM C56: unit_gbp x qty == line_gbp | 44 | 44 | 1 | 0
process:pump-sizing | motor_power_kw | 1.923 | kW | inputs from: brief | drain_transfer_pump_power_kw = 1.923 | USED | PASS | [5 empty] | BoM C57: unit_gbp x qty == line_gbp | 35 | 35 | 1 | 0
water-storage:buffer-sizing | fresh_water_storage_capacity_m3 | 40 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | fresh_water_storage_capacity_m3 = 40 | USED | PASS | [5 empty] | BoM C58: unit_gbp x qty == line_gbp | 920 | 920 | 1 | 0
water-storage:buffer-sizing | drain_water_tank_volume_each_m3 | 40 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | drain_water_tank_volume_each_m3 = 40 | USED | PASS | [5 empty] | BoM C59: unit_gbp x qty == line_gbp | 3161 | 3161 | 1 | 0
water-storage:buffer-sizing | total_water_storage_volume_m3 | 261.6 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | total_water_storage_volume_m3 = 261.6 | USED | PASS | [5 empty] | BoM C60: unit_gbp x qty == line_gbp | 1594 | 1594 | 1 | 0
water-treatment-ro:sizing | ro_membrane_area_m2 | 363.6 | m2 | inputs from: brief | ro_membrane_area_m2 = 363.6 | USED | PASS | [5 empty] | BoM C61: unit_gbp x qty == line_gbp | 447 | 447 | 1 | 0
water-treatment-ro:sizing | permeate_flow_m3_h | 8 | m3/h | inputs from: brief | ro_permeate_production_m3_per_hr = 8 | USED | PASS | [5 empty] | BoM C62: unit_gbp x qty == line_gbp | 1316 | 1316 | 1 | 0
water-treatment-ro:sizing | estimated_capex_gbp | 115727 | GBP | inputs from: brief | estimated_capex_gbp = 115727 | USED | PASS | [5 empty] | BoM C63: unit_gbp x qty == line_gbp | 1352 | 1352 | 1 | 0
[13 empty] | BoM C64: unit_gbp x qty == line_gbp | 604 | 604 | 1 | 0
[13 empty] | BoM C65: unit_gbp x qty == line_gbp | 23 | 23 | 1 | 0
[13 empty] | BoM C66: unit_gbp x qty == line_gbp | 21 | 21 | 1 | 0
[13 empty] | BoM C67: unit_gbp x qty == line_gbp | 23 | 23 | 1 | 0
[13 empty] | BoM C68: unit_gbp x qty == line_gbp | 19 | 19 | 1 | 0
[13 empty] | BoM C69: unit_gbp x qty == line_gbp | 22 | 22 | 1 | 0
[13 empty] | BoM C70: unit_gbp x qty == line_gbp | 23 | 23 | 1 | 0
[13 empty] | BoM C71: unit_gbp x qty == line_gbp | 93 | 93 | 1 | 0
[13 empty] | BoM C72: unit_gbp x qty == line_gbp | 96 | 96 | 1 | 0
[13 empty] | BoM C73: unit_gbp x qty == line_gbp | 96 | 96 | 1 | 0
[13 empty] | BoM C74: unit_gbp x qty == line_gbp | 23 | 23 | 1 | 0
[13 empty] | BoM X-151: unit_gbp x qty == line_gbp | 20.8 | 4451 | 214 | 0
[13 empty] | BoM X-152: unit_gbp x qty == line_gbp | 20.8 | 5824 | 280 | 0
[13 empty] | BoM X-153: unit_gbp x qty == line_gbp | 13.2 | 109296 | 8280 | 0
[13 empty] | BoM X-154: unit_gbp x qty == line_gbp | 20.8 | 87360 | 4200 | 0
[13 empty] | BoM X-155: unit_gbp x qty == line_gbp | 20.8 | 34445 | 1656 | 0
[13 empty] | BoM X-156: unit_gbp x qty == line_gbp | 35.2 | 7533 | 214 | 0
[13 empty] | BoM X-157: unit_gbp x qty == line_gbp | 16.4 | 7019 | 428 | 0
[13 empty] | BoM X-158: unit_gbp x qty == line_gbp | 6 | 36000 | 6000 | 0
[13 empty] | BoM X-159: unit_gbp x qty == line_gbp | 9 | 27000 | 3000 | 0
[13 empty] | BoM V-112: unit_gbp x qty == line_gbp | 40 | 8000 | 200 | 0
[13 empty] | BoM V-113: unit_gbp x qty == line_gbp | 45 | 1980 | 44 | 0
[13 empty] | BoM V-102: Sigma sub-component_gbp == line_gbp | 17540 | 17540 |  | 0
[13 empty] | BoM V-106: Sigma sub-component_gbp == line_gbp | 16000 | 16000 |  | 0
[13 empty] | BoM P-106: Sigma sub-component_gbp == line_gbp | 17268 | 17268 |  | 0
[13 empty] | BoM TK-103: Sigma sub-component_gbp == line_gbp | 22755 | 22752 |  | 0
[13 empty] | BoM P-102: Sigma sub-component_gbp == line_gbp | 2500 | 2500 |  | 0
[13 empty] | BoM TK-114: Sigma sub-component_gbp == line_gbp | 9367 | 9366 |  | 0
[13 empty] | BoM P-104: Sigma sub-component_gbp == line_gbp | 3700 | 3700 |  | 0
[13 empty] | BoM V-103: Sigma sub-component_gbp == line_gbp | 16540 | 16540 |  | 0
[13 empty] | BoM V-105: Sigma sub-component_gbp == line_gbp | 14825 | 14825 |  | 0
[13 empty] | BoM P-103: Sigma sub-component_gbp == line_gbp | 9413 | 9413 |  | 0
[13 empty] | BoM Z-101: Sigma sub-component_gbp == line_gbp | 8737 | 8737 |  | 0
[13 empty] | BoM P-101: Sigma sub-component_gbp == line_gbp | 3850 | 3850 |  | 0
[13 empty] | BoM V-101: Sigma sub-component_gbp == line_gbp | 14825 | 14825 |  | 0
[13 empty] | BoM TK-108: Sigma sub-component_gbp == line_gbp | 13615 | 13615 |  | 0
[13 empty] | BoM TK-106: Sigma sub-component_gbp == line_gbp | 27231 | 27230 |  | 0
[13 empty] | BoM TK-102: Sigma sub-component_gbp == line_gbp | 4000 | 4000 |  | 0
[13 empty] | BoM TK-101: Sigma sub-component_gbp == line_gbp | 4000 | 4000 |  | 0

## Connection trace
Connection trace — which part connects to what | [5 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · resolved-endpoint fraction (every ← / → tag must exist) + per-row status — connection rows carry a computed OK status (0 unresolved endpoints, no missing-tie evidence) 4… · full audit: Quality & Audit tab
The ledger authors every connection. INPUTS / OUTPUTS are LIVE cell-references to the connected part's own row (col A): select a cell and use Formulas ▸ Trace Precedents / Trace Dependents to draw the arrows, or click through to navigate. Each part also carries its Tag. Bidirectionally consistent. Status is a LIVE formula: OK only when every endpoint resolves to a real row/boundary AND the ledger's own completeness check is clean (columns G/H, muted).
94 authored connections · completeness: 0 part(s) missing a required tie · referential integrity: 0 broken reference(s)
Part | Tag | Status | Inputs ← (from) | Outputs → (to) | Services | Audit: unresolved endpoints (build-computed) | Audit: missing-tie evidence (build-computed) | Cell check
3 Phase Power Input | D-101 | ✓ OK | Motor Control Center | — | power | 0 |  | PASS
Chlorine Sensor | I-109 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Cip Tank (TK-101) | TK-101 | ✓ OK | Drain Transfer Pump, Permeate Outlet, Drain Collection Sump | Cip Tank (TK-102), Drain Collection Sump | water | 0 |  | PASS
Cip Tank (TK-102) | TK-102 | ✓ OK | Cip Tank (TK-101), Drain Collection Sump | Fresh Water Tank, Drain Collection Sump | water | 0 |  | PASS
Cloth Filter | V-103 | ✓ OK | Ro Membrane Elements, Motor Control Center, Drain Collection Sump | Gac Filter, Drain Collection Sump | power, water | 0 |  | PASS
Concentrate Outlet | X-103 | ✓ OK | Motor Control Center | — | power | 0 |  | PASS
Conductivity Sensor | I-104 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Control + Instrument UPS | U-201 | ✓ OK | Motor Control Center | Digital Control Panel | power, signal | 0 |  | PASS
Digital Control Panel | I-103 | ✓ OK | Electrical Control Panel, Control + Instrument UPS, Motor Control Center, Piping Network, Electrical Control Cabinet | — | power, signal | 0 |  | PASS
Distribution Manifold | M-101 | ✓ OK | Irrigation Pump | Drain Collection Sump | water | 0 |  | PASS
Drain Collection Sump | TK-114 | ✓ OK | Uv Disinfection, Fresh Water Tank, Softener Vessel, Fertigation Dosing Pump, Nutrient Tank, Hand Watering Pump, Cloth Filter, Gac Softener, Irrigation Pump, Distribution Manifold, Reverse Osmosis Skid, Ro High Pressure Pump, Gac Filter, Uf Module Bank, Cip Tank (TK-102), Cip Tank (TK-101) | Drain Water Tank, Effluent / disposal — battery limit, Uv Disinfection, Softener Vessel, Hand Watering Pump, Cloth Filter, Gac Softener, Irrigation Pump, Reverse Osmosis Skid, Ro High Pressure Pump, Gac Filter, Uf Module Bank, Cip Tank (TK-102), Cip Tank (TK-101) | water | 0 |  | PASS
Drain Transfer Pump | P-104 | ✓ OK | Drain Water Tank, Motor Control Center, Fresh Water Tank | Cip Tank (TK-101), Effluent / disposal — battery limit | power, water | 0 |  | PASS
Drain Water Tank | TK-106 | ✓ OK | Drain Collection Sump, Fresh Water Tank | Drain Transfer Pump, Effluent / disposal — battery limit | water | 0 |  | PASS
Effluent / disposal — battery limit |  | ✓ OK | Drain Collection Sump, Drain Transfer Pump, Drain Water Tank | — | water | 0 |  | PASS
Electrical Control Cabinet | I-102 | ✓ OK | Motor Control Center | Digital Control Panel | power, signal | 0 |  | PASS
Electrical Control Panel | X-105 | ✓ OK | Motor Control Center | Digital Control Panel | power, signal | 0 |  | PASS
Fertigation Dosing Pump | P-106 | ✓ OK | Motor Control Center | Hand Watering Pump, Drain Collection Sump | power, water | 0 |  | PASS
Flow Meter (I-105) | I-105 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Fresh Water Tank | TK-108 | ✓ OK | Cip Tank (TK-102), Ultrafiltration Module | Nutrient Tank, Permeate Outlet, Drain Collection Sump, Drain Transfer Pump, Drain Water Tank | water | 0 |  | PASS
Gac Filter | V-101 | ✓ OK | Cloth Filter, Motor Control Center, Drain Collection Sump | Uv Disinfection, Drain Collection Sump | power, water | 0 |  | PASS
Gac Softener | V-105 | ✓ OK | Drain Collection Sump | Softener Vessel, Drain Collection Sump | water | 0 |  | PASS
Grp Membrane Housings | F-3 | ✓ OK | Softener Vessel | Uf Module Bank | water | 0 |  | PASS
Hand Watering Pump | P-102 | ✓ OK | Fertigation Dosing Pump, Motor Control Center, Drain Collection Sump | Irrigation Pump, Drain Collection Sump | power, water | 0 |  | PASS
Irrigation Pump | P-103 | ✓ OK | Hand Watering Pump, Motor Control Center, Drain Collection Sump | Distribution Manifold, Drain Collection Sump | power, water | 0 |  | PASS
Leak Detection Sensor | I-113 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Level Transmitter | LT-201–213 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Main Switchboard | EP-101 | ✓ OK | Transformer | Motor Control Center | power | 0 |  | PASS
Mains Incomer | EP-102 | ✓ OK | — | Standby Diesel Generator | power | 0 |  | PASS
Motor Control Center | EP-104 | ✓ OK | Main Switchboard | Electrical Control Panel, 3 Phase Power Input, Control + Instrument UPS, SCADA / Plant Control System, Digital Control Panel, Piping Network, Uv Disinfection, Fertigation Dosing Pump, Hand Watering Pump, Drain Transfer Pump, Cloth Filter, Irrigation Pump, Ro High Pressure Pump, Gac Filter, Permeate Outlet, Concentrate Outlet, Electrical Control Cabinet | power, signal | 0 |  | PASS
Nutrient Tank | TK-103 | ✓ OK | Fresh Water Tank | Drain Collection Sump | water | 0 |  | PASS
Orp Sensor | I-107 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Permeate Outlet | X-104 | ✓ OK | Fresh Water Tank, Motor Control Center | Cip Tank (TK-101), Ultrafiltration Module | power, water | 0 |  | PASS
pH Analyser | AT-201 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Ph Sensor | I-106 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Piping Network | X-102 | ✓ OK | Motor Control Center | Digital Control Panel | power, signal | 0 |  | PASS
Pressure Transmitter | PT-201–217 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Reverse Osmosis Skid | Z-101 | ✓ OK | Ro High Pressure Pump, Drain Collection Sump | Ro Membrane Elements, Drain Collection Sump | water | 0 |  | PASS
Ro High Pressure Pump | P-101 | ✓ OK | Uf Module Bank, Motor Control Center, Drain Collection Sump | Reverse Osmosis Skid, Drain Collection Sump | power, water | 0 |  | PASS
Ro Membrane Elements | F-1 | ✓ OK | Reverse Osmosis Skid | Cloth Filter | water | 0 |  | PASS
SCADA / Plant Control System | EP-103 | ✓ OK | Conductivity Sensor, Flow Meter (I-105), Ph Sensor, Orp Sensor, Level Transmitter, pH Analyser, Pressure Transmitter, Silica Analyzer, Chlorine Sensor, Tds Sensor, Leak Detection Sensor, Motor Control Center | — | power, signal | 0 |  | PASS
Silica Analyzer | I-108 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Softener Vessel | V-106 | ✓ OK | Gac Softener, Drain Collection Sump | Grp Membrane Housings, Drain Collection Sump | water | 0 |  | PASS
Standby Diesel Generator | G-201 | ✓ OK | Mains Incomer | Transformer | power | 0 |  | PASS
Tds Sensor | I-110 | ✓ OK | — | SCADA / Plant Control System | signal | 0 |  | PASS
Transformer | TX-101 | ✓ OK | Standby Diesel Generator | Main Switchboard | power | 0 |  | PASS
Uf Module Bank | Z-102 | ✓ OK | Grp Membrane Housings, Drain Collection Sump | Ro High Pressure Pump, Drain Collection Sump | water | 0 |  | PASS
Ultrafiltration Module | Z-103 | ✓ OK | Permeate Outlet | Fresh Water Tank | water | 0 |  | PASS
Uv Disinfection | V-102 | ✓ OK | Gac Filter, Motor Control Center, Drain Collection Sump | Drain Collection Sump | power, water | 0 |  | PASS
Cabinets — housed devices + connector proof
6 cabinet(s) · 5 housed device(s) · 1/6 cabinets fully connected · ALL CONNECTORS PROVEN: NO — see ✗ rows
SCADA / Plant Control System [CONTROL CABINET · EP-103] — 5 device(s) housed · cabinet feeds: 12 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out | Cell check
Circuit Breaker | X-110 | distributes electrical power | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Vfd Controller | INV-2 | computes / commands | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Remote Monitoring Gateway | X-124 | computes / commands | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Power Supply Unit | X-132 | computes / commands | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Surge Protection Device | X-133 | distributes electrical power | — | — | ✗ unconnected (0 in / 0 out) | 0 | 0 | PASS
Digital Control Panel [CONTROL CABINET · I-103] — 0 device(s) housed · cabinet feeds: 6 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —
Electrical Control Panel [CONTROL CABINET · X-105] — 0 device(s) housed · cabinet feeds: 1 in / 1 out · ✓ ALL CONNECTED
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —
PLC Controller [CONTROL CABINET · X-115] — 0 device(s) housed · cabinet feeds: 0 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —
HMI Touchscreen [CONTROL CABINET · X-121] — 0 device(s) housed · cabinet feeds: 0 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —
Siemens S7 1200 PLC [CONTROL CABINET · X-122] — 0 device(s) housed · cabinet feeds: 0 in / 0 out · ✗ INCOMPLETE
Housed device | Tag | Function | Inputs ← (from) | Outputs → (to) | Connectors | Audit: n in | Audit: n out
— no discrete devices itemised (cabinet feeds the loads directly) —

## Quantities
Contract inputs — traceability (where-from / where-to) | [7 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · quantity provenance (source + where-from + used-by per row) — provenance-verified quantity rows 113/113; cell completeness+type contract 339/339 · score = min over check… · full audit: Quality & Audit tab
Where each INPUT came FROM (its source / the quantities it was computed from) and what it FEEDS into downstream. Apart from the brief, every value traces back to the briefing document. — 109/111 inputs (98%) trace to the brief.
Input | Value | Unit | Family | Source | Where-from (source / inputs) | Source detail | Used by (where-to) | Cell check
ro_permeate_capacity_m3_h | 8 | m³/h | flow_rate | brief | ← brief (stated requirement) | reverse-osmosis permeate capacity (an industrial RO skid 8 m³/h); lock-gate HARD slot (exit 22) | permeate_outlet_line_flow_m3_h, permeate_manifold_line_flow_m3_h | PASS
irrigation_demand_m3_h | 90 | m³/h | flow_rate | calculator | ← calculated (inputs in Source detail — not yet machine-linked) | peak irrigation demand = 45 m³/h per department × 2 departments; lock-gate HARD slot (exit 22) | uv_disinfection_throughput_m3_h, irrigation_pump_motor_kw, irrigation_pump_flow_m3_h | PASS
uv_disinfection_throughput_m3_h | 90 | m³/h | flow_rate | calculator | ← irrigation_demand_m3_h ✓ LIVE formula (Value is computed in-cell) | medium-pressure UV-C reactor sized to the peak recirculated flow (= irrigation demand 90 m³/h) for Legionella control at ≈40 mJ/cm² | uv_disinfection_power_kw → part: Uv Disinfection | PASS
uv_disinfection_power_kw | 4.05 | kW | power | calculator | ← uv_disinfection_throughput_m3_h ✓ LIVE formula (Value is computed in-cell) | UV-C lamp electrical draw ≈ 0.045 kW per m³/h at the Legionella dose (90 m³/h × 0.045) | → part: Uv Disinfection | PASS
uv_disinfection_count | 1 | off | count | calculator | ← measured: derived | one duty UV-C reactor on the common recirculation main (all stored/recirculated water passes it before distribution) | → part: Uv Disinfection | PASS
hand_watering_discharge_pressure_bar | 3 | bar | pressure | brief | ← brief (stated requirement) | hand-watering ring-main delivery pressure (brief-stated 3 bar; sets the hand-watering pump head) | → informs calculations / design rules (see Source detail) | PASS
fresh_water_storage_capacity_m3 | 40 | m3 | volume | brief | ← tool: water-storage:buffer-sizing | brief-pinned 40 (held — water-storage:buffer-sizing suggested 196.8: a 5× divergence, rejected as a gross override of an explicit brief spec) | → informs calculations / design rules (see Source detail) | PASS
water_storage_capacity_m3 | 120 | m³ | volume | calculator | ← fresh_water_tank_volume_each_m3, fresh_water_tank_count, drain_water_tank_count ✓ LIVE formula (Value is computed in-cell) | total water storage = 3 galvanised tanks (1 fresh + 2 drain) × 40 m³ = 120 m³ | water_storage_delivered_m3 | PASS
reverse_osmosis_skid_volume_m3 | 10 | m³ | volume | brief | ← brief (stated requirement) | reverse-osmosis packaged skid envelope (3.8 m × 1.4 m × 2.0 m, an industrial RO skid, 8 m³/h @ 75% recovery) | → part: Reverse Osmosis Skid | PASS
reverse_osmosis_skid_count | 1 |  | dimensionless | brief | ← brief (stated requirement) | one RO purification skid | → part: Reverse Osmosis Skid | PASS
ro_high_pressure_pump_throughput_m3_h | 11 | m³/h | flow_rate | brief | ← brief (stated requirement) | RO frequency-controlled high-pressure pump (10.6 bar working pressure, ~10.7 m³/h feed) | pressure_vessels_line_flow_m3_h → part: Ro High Pressure Pump | PASS
ro_high_pressure_pump_power_kw | 4.2 | kW | power | brief | ← brief (stated requirement) | RO high-pressure pump motor (frequency-controlled; 4.2 kW consumption within the RO skid 5.5 kW installed) | → part: Ro High Pressure Pump | PASS
ro_high_pressure_pump_count | 1 |  | dimensionless | brief | ← brief (stated requirement) | one frequency-controlled RO high-pressure pump | → part: Ro High Pressure Pump | PASS
gac_filter_vessel_volume_m3 | 1.8 | m³ | volume | calculator | ← gac_softener_throughput_m3_h | granular-activated-carbon filter vessel (1 × 42-inch tank, 14.5 m³/h) | → informs calculations / design rules (see Source detail) | PASS
softener_vessel_volume_each_m3 | 1.5 | m³ | volume | calculator | ← calculated (inputs in Source detail — not yet machine-linked) | glass-fibre softener vessel (350 L resin each, 14 m³/h duplex) | → part: Softener Vessel | PASS
softener_vessel_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | two duplex softener vessels | → part: Softener Vessel | PASS
fresh_water_tank_volume_each_m3 | 40 | m³ | volume | brief | ← brief (stated requirement) | fresh-water galvanised storage tank (3.64 m dia × 3.88 m, 40 m³) | water_storage_capacity_m3 → part: Fresh Water Tank | PASS
fresh_water_tank_count | 1 |  | dimensionless | brief | ← brief (stated requirement) | one fresh-water storage tank | water_storage_capacity_m3 → part: Fresh Water Tank | PASS
drain_water_tank_volume_each_m3 | 40 | m3 | volume | brief | ← tool: water-storage:buffer-sizing | brief-pinned 40 (held — water-storage:buffer-sizing suggested 64.8: an explicitly-dimensioned brief storage vessel is held EXACTLY (water-storage:buffer-sizing's 64.8 is a generic buffer-model refinement, rejected)) | → part: Drain Water Tank | PASS
drain_water_tank_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | two drain-water storage tanks | water_storage_capacity_m3 → part: Drain Water Tank | PASS
fertigation_dosing_pump_throughput_m3_h | 45 | m³/h | flow_rate | brief | ← brief (stated requirement) | A/B fertigation circulation pump (Lowara e-SHE 50-160/75, 45 m³/h @ 3.5 bar) | fertigation_dosing_capacity_m3_per_hr, fertigation_dosing_total_m3_h → part: Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5 | PASS
fertigation_dosing_pump_power_kw | 7.5 | kW | power | brief | ← tool: process:pump-sizing | brief-pinned 7.5 (held — process:pump-sizing suggested 3.846: 3.846 < the brief 7.5 power rating — a tool must not under-size a must-meet brief spec) | connected_electrical_load_kw → part: Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5 | PASS
fertigation_dosing_pump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 A/B fertigation dosing units (one per department) | fertigation_dosing_capacity_m3_per_hr, connected_electrical_load_kw → part: Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5 | PASS
fertigation_dosing_capacity_m3_per_hr | 90 | m³/h | flow_rate | calculator | ← fertigation_dosing_pump_throughput_m3_h, fertigation_dosing_pump_count ✓ LIVE formula (Value is computed in-cell) | total fertigation dosing capacity = 2 units × 45 m³/h = 90 m³/h | → part: Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5 | PASS
acid_dosing_pump_throughput_m3_h | 0.04 | m³/h | flow_rate | brief | ← brief (stated requirement) | acid metering pump (Iwaki EWN-C21VCER, 100 L barrel, ~40 L/h) | → informs calculations / design rules (see Source detail) | PASS
acid_dosing_pump_power_kw | 0.04 | kW | power | brief | ← brief (stated requirement) | acid metering pump motor (frequency-controlled) | → informs calculations / design rules (see Source detail) | PASS
acid_dosing_pump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 acid dosing pumps (one per A/B fertigation unit) | → informs calculations / design rules (see Source detail) | PASS
chemical_dosing_pump_throughput_m3_h | 0.04 | m³/h | flow_rate | brief | ← brief (stated requirement) | chemical/nutrient metering pump (Iwaki EWN-C21VHERA, 100 L barrel, ~40 L/h) | → informs calculations / design rules (see Source detail) | PASS
chemical_dosing_pump_power_kw | 0.04 | kW | power | brief | ← brief (stated requirement) | chemical metering pump motor (frequency-controlled) | → informs calculations / design rules (see Source detail) | PASS
chemical_dosing_pump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 chemical/nutrient dosing pumps (one per A/B fertigation unit) | → informs calculations / design rules (see Source detail) | PASS
nutrient_tank_volume_each_m3 | 1 | m³ | volume | brief | ← brief (stated requirement) | nutrient stock tank (1,000 L polyester, 4 × A + 4 × B) | → part: Nutrient Tank | PASS
nutrient_tank_count | 8 |  | dimensionless | brief | ← brief (stated requirement) | eight 1,000 L nutrient stock tanks | → part: Nutrient Tank | PASS
hand_watering_pump_throughput_m3_h | 25 | m³/h | flow_rate | brief | ← brief (stated requirement) | hand-watering frequency-controlled pump (25 m³/h @ 3 bar) | hand_watering_pump_motor_kw, hand_watering_ring_main_length_m, hand_watering_ring_main_dn_mm, hand_watering_riser_count → part: Hand Watering Pump | PASS
hand_watering_pump_count | 1 |  | dimensionless | brief | ← brief (stated requirement) | one hand-watering pump | connected_electrical_load_kw → part: Hand Watering Pump | PASS
drain_collection_sump_volume_each_m3 | 5 | m3 | volume | brief | ← tool: irrigation:ebb-flow-demand | brief-pinned 5 (held — irrigation:ebb-flow-demand suggested 600: a 120× divergence, rejected as a gross override of an explicit brief spec) | → part: Drain Collection Sump | PASS
drain_collection_sump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 drain pits (one per cultivation room) | → part: Drain Collection Sump | PASS
drain_transfer_pump_throughput_m3_h | 45 | m³/h | flow_rate | brief | ← brief (stated requirement) | drain-pit submersible transfer pump (45 m³/h) | drain_manifold_line_flow_m3_h, drain_collection_sump_line_flow_m3_h → part: Drain Transfer Pump | PASS
drain_transfer_pump_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 submersible drain pumps | connected_electrical_load_kw → part: Drain Transfer Pump | PASS
cloth_filter_throughput_m3_h | 80 | m³/h | flow_rate | brief | ← brief (stated requirement) | drain-water cloth filter (80 m³/h) on HDPE tank, returns to drain tank | → part: Cloth Filter | PASS
cloth_filter_count | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 cloth-filter units | → part: Cloth Filter | PASS
cultivation_container_count | 6000 |  | dimensionless | brief | ← brief (stated requirement) | 6,000 ebb/flow cultivation containers (2 dept × 10 tunnels × 5 layers × 4 rows × 15) — the irrigation network sizing driver | → informs calculations / design rules (see Source detail) | PASS
actuated_distribution_valve_count | 200 |  | dimensionless | brief | ← brief (stated requirement) | 200 electrically-actuated 2.5-inch ebb/flow distribution valves (30 containers each) | distribution_main_length_m, distribution_main_dn_mm, distribution_riser_length_m, distribution_riser_dn_mm, distribution_zone_lateral_length_m, distribution_zone_lateral_dn_mm, distribution_drain_riser_length_m, distribution_drain_riser_dn_mm, distribution_drain_collection_length_m, distribution_drain_collection_dn_mm, distribution_drain_main_length_m, distribution_drain_main_dn_mm, distribution_network_length_km, distribution_zone_kits, distribution_position_connections, distribution_drain_outlet_connections, distribution_manifold_count, distribution_manifold_throughput_m3_h | PASS
distribution_delivery_groups | 2 |  | dimensionless | brief | ← brief (stated requirement) | 2 delivery departments — each A/B fertigation unit feeds its own department main (DN125 mainline per department) | distribution_branch_runs | PASS
distribution_branch_runs | 20 |  | dimensionless | brief | ← brief (stated requirement) | 10 cultivation tunnels per department × 2 departments = 20 branch (tunnel) runs | → informs calculations / design rules (see Source detail) | PASS
distribution_levels_per_branch | 5 |  | dimensionless | brief | ← brief (stated requirement) | 5 cultivation layers per tunnel — one zone valve per layer per riser | → informs calculations / design rules (see Source detail) | PASS
distribution_risers_per_branch | 2 |  | dimensionless | brief | ← brief (stated requirement) | two DN125 riser connections per cultivation tunnel (brief: "two riser connections per tunnel") | → informs calculations / design rules (see Source detail) | PASS
distribution_positions_per_zone | 30 |  | dimensionless | brief | ← brief (stated requirement) | 30 containers per actuated valve section (the flood-fill zone) | → informs calculations / design rules (see Source detail) | PASS
distribution_zone_rows | 2 |  | dimensionless | brief | ← brief (stated requirement) | each valve section feeds two rows of containers ("30 containers (two rows of 15) via a DN75 distribution line") | → informs calculations / design rules (see Source detail) | PASS
distribution_position_pitch_mm | 2760 | mm | length | brief | ← brief (stated requirement) | cultivation container length 2760 mm (container 2760 × 1290 mm) — the along-row position pitch | → informs calculations / design rules (see Source detail) | PASS
distribution_position_width_mm | 1290 | mm | length | brief | ← brief (stated requirement) | cultivation container width 1290 mm — sets the branch (tunnel) pitch across the rows | → informs calculations / design rules (see Source detail) | PASS
distribution_zone_valve_dn_mm | 65 | mm | dimension | brief | ← brief (stated requirement) | 2.5-inch electric zone valves → DN65 (the brief's stated valve bore) | → informs calculations / design rules (see Source detail) | PASS
ro_recovery_percent | 75 | % | dimensionless | brief | ← brief (stated requirement) | RO recovery factor (75%) | → design output (feeds cost / financial / drawings) | PASS
gac_softener_throughput_m3_h | 14.5 | m³/h | flow_rate | brief | ← brief (stated requirement) | GAC / softener treatment throughput (~14.5 m³/h) | gac_filter_vessel_volume_m3, softener_vessel_line_flow_m3_h → part: Gac Softener | PASS
connected_electrical_load_kw | 53 | kW | power | calculator | ← fertigation_dosing_pump_power_kw, fertigation_dosing_pump_count, hand_watering_pump_count, drain_transfer_pump_count | sum of pump + dosing + control loads ≈ 53 kW — a pumping/dosing plant, NOT a megawatt facility (lighting + HVAC are out of scope) | total_supply_demand_kw, main_incomer_breaker_a | PASS
building_out_of_scope | 1 |  | dimensionless | brief | ← brief (stated requirement) | the building, civils and cultivation rack framework are supplied by others — OUT of scope (no hall is synthesised around the water plant) | → informs calculations / design rules (see Source detail) | PASS
total_supply_demand_kw | 53 | kW | power | convergence-report | ← connected_electrical_load_kw, total_electrical_demand_kw | alias of connected_electrical_load_kw = 53 kW by construction (the tool-claimed plant load); the as-routed converged demand 54.699 kW (plant load + distribution parasitic, 3.2% off) RECONCILES within ±10% and is recorded here — the alias itself never moves | total_supply_demand_kva | PASS
incident_energy_cal_cm2 | 0.741 | cal/cm2 | area | tool:arc-flash:ieee-1584 | ← tool: arc-flash:ieee-1584 | computed by arc-flash:ieee-1584 (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
ph_control_kp | 0.29646 |  | dimensionless | tool:control-systems:pid-tuning | ← tool: control-systems:pid-tuning | computed by control-systems:pid-tuning (inputs from brief) | → informs calculations / design rules (see Source detail) | PASS
transformer_kva | 75 | kVA | power | tool:electrical:transformer-sizing | ← tool: electrical:transformer-sizing | computed by electrical:transformer-sizing (inputs from brief) | → part: Transformer | PASS
transformer_secondary_current_a | 108.25 | A | current | tool:electrical:transformer-sizing | ← tool: electrical:transformer-sizing | computed by electrical:transformer-sizing (inputs from brief) | → part: Transformer | PASS
main_feeder_cable_csa_mm2 | 25 | mm2 | area | tool:electrical:cable-sizing | ← tool: electrical:cable-sizing | computed by electrical:cable-sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
cable_voltdrop_pct | 2.03 | % | dimensionless | tool:electrical:cable-sizing | ← tool: electrical:cable-sizing | computed by electrical:cable-sizing (inputs from brief) | → part: Cable Glands, Cable Trays | PASS
gac_vessel_diameter_m | 1.3587 | m | length | tool:gac-filter:liquid-phase-sizing | ← tool: gac-filter:liquid-phase-sizing | computed by gac-filter:liquid-phase-sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
softener_salt_consumption_max_kg_per_regen | 46.1993 | kg | mass | tool:ion-exchange:softener-sizing | ← tool: ion-exchange:softener-sizing | computed by ion-exchange:softener-sizing (inputs from brief) | → informs calculations / design rules (see Source detail) | PASS
irrigation_pump_motor_kw | 9.653 | kW | power | tool:irrigation:pump-sizing | ← tool: irrigation:pump-sizing | computed by irrigation:pump-sizing from irrigation_demand_m3_h | total_system_mass_kg | PASS
irrigation_pump_flow_m3_h | 90 | m3/h | volflow | tool:irrigation:pump-sizing | ← tool: irrigation:pump-sizing | computed by irrigation:pump-sizing from irrigation_demand_m3_h | → informs calculations / design rules (see Source detail) | PASS
cloth_filter_area_m2 | 3.4657 | m2 | area | tool:mechanical-filtration:cloth-screen | ← tool: mechanical-filtration:cloth-screen | computed by mechanical-filtration:cloth-screen (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
filter_hydraulic_loading_m_h | 23.0832 | m/h | velocity | tool:mechanical-filtration:cloth-screen | ← tool: mechanical-filtration:cloth-screen | computed by mechanical-filtration:cloth-screen (inputs from brief) | → part: Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5 | PASS
acid_dose_rate_ml_min | 640 | mL/min | volflow | tool:ph-titration:sizing | ← tool: ph-titration:sizing | computed by ph-titration:sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
gac_vessel_mass_kg | 600.811 | kg | mass | tool:pressure-vessel:design | ← tool: pressure-vessel:design | computed by pressure-vessel:design (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
total_system_mass_kg | 1500.8 | kg | mass | tool:mass-aggregator:envelope-check | ← tool: mass-aggregator:envelope-check | computed by mass-aggregator:envelope-check from irrigation_pump_motor_kw | → design output (feeds cost / financial / drawings) | PASS
ro_membrane_area_m2 | 363.6 | m2 | area | tool:water-treatment-ro:sizing | ← tool: water-treatment-ro:sizing | computed by water-treatment-ro:sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
ro_permeate_production_m3_per_hr | 8 | m3/h | volflow | tool:water-treatment-ro:sizing | ← tool: water-treatment-ro:sizing | computed by water-treatment-ro:sizing (inputs from brief) | → informs calculations / design rules (see Source detail) | PASS
estimated_capex_gbp | 115727 | GBP | currency | tool:water-treatment-ro:sizing | ← tool: water-treatment-ro:sizing | computed by water-treatment-ro:sizing (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
total_water_storage_volume_m3 | 261.6 | m3 | volume | tool:water-storage:buffer-sizing | ← tool: water-storage:buffer-sizing | computed by water-storage:buffer-sizing (inputs from brief) | → informs calculations / design rules (see Source detail) | PASS
drain_transfer_pump_power_kw | 1.923 | kW | power | tool:process:pump-sizing | ← tool: process:pump-sizing | computed by process:pump-sizing (inputs from brief) | → part: Drain Transfer Pump | PASS
softener_vessel_mass_kg | 556.127 | kg | mass | tool:pressure-vessel:design | ← tool: pressure-vessel:design | computed by pressure-vessel:design (inputs from brief) | → design output (feeds cost / financial / drawings) | PASS
hand_watering_pump_motor_kw | 2.8 | kW | power | demand-coverage | ← hand_watering_pump_throughput_m3_h | demand-coverage: hydraulic motor floor P = Q·ΔP/(36·η) @ ΔP = 2.5 bar, η = 0.62, from hand_watering_pump_throughput_m3_h = 25 m³/h (a sizing-tool value always wins when present) | → informs calculations / design rules (see Source detail) | PASS
permeate_outlet_line_flow_m3_h | 8 | m3/h | flow_rate | demand-coverage | ← ro_permeate_capacity_m3_h | demand-coverage: service-line duty for Permeate Outlet = ro_permeate_capacity_m3_h (8 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
drain_manifold_line_flow_m3_h | 45 | m3/h | flow_rate | demand-coverage | ← drain_transfer_pump_throughput_m3_h | demand-coverage: service-line duty for Drain Manifold = drain_transfer_pump_throughput_m3_h (45 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
pressure_vessels_line_flow_m3_h | 11 | m3/h | flow_rate | demand-coverage | ← ro_high_pressure_pump_throughput_m3_h | demand-coverage: service-line duty for Pressure Vessels = ro_high_pressure_pump_throughput_m3_h (11 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
permeate_manifold_line_flow_m3_h | 8 | m3/h | flow_rate | demand-coverage | ← ro_permeate_capacity_m3_h | demand-coverage: service-line duty for Permeate Manifold = ro_permeate_capacity_m3_h (8 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
cleaning_tank_line_flow_m3_h | 4 | m3/h | flow_rate | demand-coverage | ← (cip one-charge rule) | demand-coverage: CIP recirculation duty — one cleaning-solution charge (2 m³, the one-charge rule: ~15% of the plant hourly design flow bounded 0.5–2 m³) turned over in 30 min → 4 m³/h service-line flow for Cleaning Tank | → informs calculations / design rules (see Source detail) | PASS
cip_tank_line_flow_m3_h | 4 | m3/h | flow_rate | demand-coverage | ← (cip one-charge rule) | demand-coverage: CIP recirculation duty — one cleaning-solution charge (2 m³, the one-charge rule: ~15% of the plant hourly design flow bounded 0.5–2 m³) turned over in 30 min → 4 m³/h service-line flow for Cip Tank | → informs calculations / design rules (see Source detail) | PASS
water_storage_delivered_m3 | 120 | m3 | volume_m3 | demand-coverage | ← water_storage_capacity_m3 | demand-coverage: DELIVERED storage total for brief metric water_storage_capacity_m3 = Fresh Water Tank 1× 40 m³ (contract quantity family) + Drain Water Tank 2× 40 m³ (contract quantity family) — sums the design's storage-vessel principals (capacity × qty), never the target echo, so a genuine shortfall stays visible | → informs calculations / design rules (see Source detail) | PASS
fertigation_dosing_total_m3_h | 90 | m3/h | flow_rate | demand-coverage | ← fertigation_dosing_pump_throughput_m3_h | demand-coverage: DELIVERED total = 45 m³/h per unit × 2 units (fertigation_dosing_pump_throughput_m3_h × fertigation_dosing_pump_count), corroborated by fertigation_dosing_capacity_m3_per_hr = 90 m³/h — the explicit system total, so no reader mistakes the per-unit figure for the delivery | → part: Fertigation Dosing Pump, Fertigation dosing / injection pump — vertical multistage, 30 m3/h @ 53.1 m, 7.5 | PASS
distribution_main_length_m | 214 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): delivery mains (department spines) = 2 group(s) × (10 branches × 7.7 m branch pitch + 30 m plant-room stand-off) = 214 m; DN125 at 45 m³/h ≤ 1.3 m/s (surge-limited delivery main on a cycling valve network) · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_main_dn_mm | 125 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN125 from d = √(4·Q/π·v) at the segment service velocity — see distribution_main_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_riser_length_m | 280 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): delivery risers = 40 risers (200 zones ÷ 5 levels) × 7 m (5 levels × 1.3 m tier pitch + 0.5 m) = 280 m; DN125 at 45 m³/h ≤ 1.3 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_riser_dn_mm | 125 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN125 from d = √(4·Q/π·v) at the segment service velocity — see distribution_riser_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_zone_lateral_length_m | 8280 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): zone laterals = 200 zones × (30 positions/zone ÷ 2 rows × 2.76 m position pitch) = 200 × 41.4 m = 8280 m; DN75 at the 45 m³/h open-zone flood-fill duty ≤ 3.0 m/s (short-duration fill) · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_zone_lateral_dn_mm | 75 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN75 from d = √(4·Q/π·v) at the segment service velocity — see distribution_zone_lateral_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_drain_riser_length_m | 4200 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): drain/return risers (mirror of the delivery grid) = 600 gravity drops (an outlet per 2 positions per level) × 7 m = 4200 m; DN110 gravity at 45 m³/h ≤ 1.4 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_drain_riser_dn_mm | 110 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN110 from d = √(4·Q/π·v) at the segment service velocity — see distribution_drain_riser_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_drain_collection_length_m | 1656 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): drain collection lines = 2 floor lines/branch × 41.4 m × 20 branches = 1656 m; DN110 gravity ≤ 1.4 m/s · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_drain_collection_dn_mm | 110 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN110 from d = √(4·Q/π·v) at the segment service velocity — see distribution_drain_collection_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_drain_main_length_m | 214 | m | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): main drain headers = the delivery-spine mirror (214 m); DN160 at 45 m³/h ≤ 0.8 m/s part-full gravity equivalent · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
distribution_drain_main_dn_mm | 160 | mm | dimension | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN160 from d = √(4·Q/π·v) at the segment service velocity — see distribution_drain_main_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
distribution_network_length_km | 14.844 | km | length | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): total zoned-distribution pipework = mains 214 + risers 280 + zone laterals 8280 + drain risers 4200 + drain collection 1656 + drain mains 214 = 14844 m = 14.844 km · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → informs calculations / design rules (see Source detail) | PASS
distribution_zone_kits | 200 |  | count | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): one zone connection kit (valve stub-in, unions, supports) per sectioning valve = 200 | → informs calculations / design rules (see Source detail) | PASS
distribution_position_connections | 6000 |  | count | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): one delivery inlet stub + fitting per served position = 6000 | → informs calculations / design rules (see Source detail) | PASS
distribution_drain_outlet_connections | 3000 |  | count | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): one gravity drain outlet per 2 served positions = 3000 | → informs calculations / design rules (see Source detail) | PASS
distribution_manifold_count | 2 |  | count | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): one distribution manifold station (delivery header, isolation + non-return valves, drain tie-in) per delivery group = 2 | → part: Distribution Manifold | PASS
distribution_manifold_throughput_m3_h | 45 | m3/h | flow_rate | demand-coverage | ← actuated_distribution_valve_count | parametric — not routed (zoned-delivery distribution network, engineered allowance): each distribution manifold passes its group's 45 m³/h delivery duty (irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric)) | → part: Distribution Manifold | PASS
hand_watering_ring_main_length_m | 428 | m | length | demand-coverage | ← hand_watering_pump_throughput_m3_h | parametric — not routed (zoned-delivery distribution network, engineered allowance): hand-watering ring main = 2 delivery group(s)/department(s) × 2 legs (ring out-and-return along the 107 m delivery spine, serving every branch head) = 428 m · 200 zones (actuated_distribution_valve_count) × 30 positions/zone (6000 served positions); 2 delivery group(s); 20 branch runs × 5 level(s); fill duty 45 m³/h/group from irrigation_pump_flow_m3_h = 90 m³/h delivered ÷ 2 groups (the irrigation_demand_m3_per_hr = 45 m³/h per-group brief metric) | → design output (feeds cost / financial / drawings) | PASS
hand_watering_ring_main_dn_mm | 90 | mm | dimension | demand-coverage | ← hand_watering_pump_throughput_m3_h | parametric — not routed (zoned-delivery distribution network, engineered allowance): DN90 from d = √(4·Q/π·v) at the 25 m³/h hand-watering duty (hand_watering_pump_throughput_m3_h) ≤ 1.3 m/s ring velocity — see hand_watering_ring_main_length_m for the run derivation | → informs calculations / design rules (see Source detail) | PASS
hand_watering_riser_count | 44 |  | count | demand-coverage | ← hand_watering_pump_throughput_m3_h | parametric — not routed (zoned-delivery distribution network, engineered allowance): hand-watering tap risers (each a hand valve + quick connector) = 2 per branch × 20 branches + 2 per delivery group at the plant/irrigation room (4) = 44 | → informs calculations / design rules (see Source detail) | PASS
main_incomer_breaker_a | 106 | A | current | calculator | ← connected_electrical_load_kw ✓ LIVE formula (Value is computed in-cell) | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_frame_a → part: Mains Incomer | PASS
main_incomer_breaker_frame_a | 125 | A | current | calculator | ← main_incomer_breaker_a | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | → part: Mains Incomer | PASS
softener_vessel_line_flow_m3_h | 14.5 | m3/h | flow_rate | demand-coverage | ← gac_softener_throughput_m3_h | demand-coverage: service-line duty for Softener Vessel = gac_softener_throughput_m3_h (14.5 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
drain_collection_sump_line_flow_m3_h | 45 | m3/h | flow_rate | demand-coverage | ← drain_transfer_pump_throughput_m3_h | demand-coverage: service-line duty for Drain Collection Sump = drain_transfer_pump_throughput_m3_h (45 m³/h) — the one delivered flow in this endpoint's distinctive-token family (the duty that serves/fills/drains it) | → informs calculations / design rules (see Source detail) | PASS
interconnect_pipe_length_m | 1021.9 | m | derived | route-manifest | ← brief | measured routed fluid + thermal pipe length | → design output (feeds cost / financial / drawings) | PASS
total_supply_demand_kva | 75 | kVA | power | design-loop | ← total_supply_demand_kw ✓ LIVE formula (Value is computed in-cell) | incomer kVA = next standard rating ≥ load × 1.25: 53 kW × 1.25 = 66.25 kVA → 75 kVA (standard ladder 50/75/100/160/250…; kVA ≥ kW for any power factor — the assumption-free adequacy basis the deterministic check verifies) | → design output (feeds cost / financial / drawings) | PASS

## Calculations
Worked calculations — every value recomputed live + checked | [7 empty] | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · worked-calc coverage (every definition resolves to a computed result; inputs populated) + tool-flow consumption — worked-calc definitions resolve to a computed result 13… · full audit: Quality & Audit tab
Yellow = editable input. Green col B = LIVE formula. 'Engine value' = the value the engine stored; Δ should be ~0 (inputs are display-rounded to 4 s.f.). Legacy calcs (no input map) are RECOMPUTED LIVE from their substitution and cross-checked against the engine value (col H verdict).
Shared constants (referenced by formulas below)
Constant | Value | Unit | Note | Cell check
rho | 1000 | kg/m³ | process-fluid density (median of 3 engine worked-calc input(s)) | PASS
rho_air | 1.2 | kg/m³ | air density | PASS
g | 9.8066 | m/s² | gravity | PASS
pi | 3.1416 | - | pi (use PI() in formulas) | PASS
mu | 0.001 | Pa·s | dynamic viscosity (water) | PASS
Tool data-flow — where each tool's inputs came from and where its outputs go
Each row: a tool OUTPUT, the INPUT it was computed from (— from), and where that value GOES (→ Consumed by). Status: USED/TRACED = the output flows on; ORPHANED = it appears nowhere downstream; STALE = the downstream value disagrees.
Tool | Output field | Value | Unit | Input — from | → Consumed by | Status | Cell check
arc-flash:ieee-1584 | incident_energy_cal_cm2 | 0.74138 | cal/cm2 | inputs from: brief | incident_energy_cal_cm2 = 0.741 | USED | PASS
control-systems:pid-tuning | kp | 0.29646 |  | inputs from: brief | ph_control_kp = 0.296464 | USED | PASS
electrical:cable-sizing | main_feeder_cable_csa_mm2 | 25 | mm2 | inputs from: electrical:transformer-sizing + brief | main_feeder_cable_csa_mm2 = 25 | USED | PASS
electrical:cable-sizing | cable_voltdrop_pct | 2.0297 | % | inputs from: electrical:transformer-sizing + brief | cable_voltdrop_pct = 2.03 | USED | PASS
electrical:transformer-sizing | transformer_kva | 75 | kVA | inputs from: brief | transformer_kva = 75 | USED | PASS
electrical:transformer-sizing | transformer_secondary_current_a | 108.2532 | A | inputs from: brief | transformer_secondary_current_a = 108.25 | USED | PASS
first-principles:disinfection | uv_disinfection_throughput_m3_h | 90 | m³/h | medium-pressure UV-C reactor sized to the peak recirculated flow (= irrigation demand 90 m³/h) for Legionella control at ≈40 mJ/cm² | uv_disinfection_throughput_m3_h = 90 | USED | PASS
first-principles:disinfection | uv_disinfection_power_kw | 4.1 | kW | UV-C lamp electrical draw ≈ 0.045 kW per m³/h at the Legionella dose (90 m³/h × 0.045) | uv_disinfection_power_kw = 4.1 | USED | PASS
first-principles:disinfection | uv_disinfection_count | 1 | off | one duty UV-C reactor on the common recirculation main (all stored/recirculated water passes it before distribution) | uv_disinfection_count = 1 | USED | PASS
first-principles:electrical | connected_electrical_load_kw | 53 | kW | sum of pump + dosing + control loads ≈ 53 kW — a pumping/dosing plant, NOT a megawatt facility (lighting + HVAC are out of scope) | connected_electrical_load_kw = 53 | USED | PASS
first-principles:process | irrigation_demand_m3_h | 90 | m³/h | peak irrigation demand = 45 m³/h per department × 2 departments; lock-gate HARD slot (exit 22) | irrigation_demand_m3_h = 90 | USED | PASS
first-principles:process | water_storage_capacity_m3 | 120 | m³ | total water storage = 3 galvanised tanks (1 fresh + 2 drain) × 40 m³ = 120 m³ | water_storage_capacity_m3 = 120 | USED | PASS
first-principles:process | softener_vessel_volume_each_m3 | 1.5 | m³ | glass-fibre softener vessel (350 L resin each, 14 m³/h duplex) | softener_vessel_volume_each_m3 = 1.5 | USED | PASS
first-principles:process | fertigation_dosing_capacity_m3_per_hr | 90 | m³/h | total fertigation dosing capacity = 2 units × 45 m³/h = 90 m³/h | fertigation_dosing_capacity_m3_per_hr = 90 | USED | PASS
first-principles:process | total_supply_demand_kw | 53 | kW | total connected electrical demand of the water plant | total_supply_demand_kw = 53 | USED | PASS
first-principles:process | main_incomer_breaker_a | 106 | A | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_a = 106 | USED | PASS
first-principles:process | main_incomer_breaker_frame_a | 125 | A | main incomer sized from the connected electrical load 53 kW: I = P·1000/(√3·400·0.9)·1.25 = 106 A → next standard 125 A ACB frame | main_incomer_breaker_frame_a = 125 | USED | PASS
first-principles:solids | gac_filter_vessel_volume_m3 | 1.8 | m³ | granular-activated-carbon filter vessel (1 × 42-inch tank, 14.5 m³/h) | gac_filter_vessel_volume_m3 = 1.8 | USED | PASS
gac-filter:liquid-phase-sizing | gac_vessel_diameter_m | 1.3587 | m | inputs from: brief | gac_vessel_diameter_m = 1.35875 | USED | PASS
ion-exchange:softener-sizing | softener_salt_consumption_max_kg_per_regen | 46.2 | kg | inputs from: brief | softener_salt_consumption_max_kg_per_regen = 46.1993 | USED | PASS
irrigation:ebb-flow-demand | drain_collection_sump_volume_each_m3 | 5 | m3 | inputs from: brief | drain_collection_sump_volume_each_m3 = 5 | USED | PASS
irrigation:pump-sizing | motor_power_kw | 9.653 | kW | inputs from: irrigation:ebb-flow-demand + brief | irrigation_pump_motor_kw = 9.653 | USED | PASS
irrigation:pump-sizing | pump_flow_m3_h | 90 | m3/h | inputs from: irrigation:ebb-flow-demand + brief | irrigation_pump_flow_m3_h = 90 | USED | PASS
mass-aggregator:envelope-check | total_system_mass_kg | 1500.811 | kg | inputs from: irrigation:pump-sizing, pressure-vessel:design + brief | total_system_mass_kg = 1500.8 | USED | PASS
mechanical-filtration:cloth-screen | cloth_filter_area_m2 | 3.4657 | m2 | inputs from: brief | cloth_filter_area_m2 = 3.46572 | USED | PASS
mechanical-filtration:cloth-screen | filter_hydraulic_loading_m_h | 23.0832 | m/h | inputs from: brief | filter_hydraulic_loading_m_h = 23.0832 | USED | PASS
ph-titration:sizing | acid_dose_rate_ml_min | 640 | mL/min | inputs from: brief | acid_dose_rate_ml_min = 640 | USED | PASS
pressure-vessel:design | mass_kg | 600.811 | kg | inputs from: gac-filter:liquid-phase-sizing + brief | gac_vessel_mass_kg = 600.811 | USED | PASS
pressure-vessel:design | mass_kg | 556.127 | kg | inputs from: gac-filter:liquid-phase-sizing + brief | softener_vessel_mass_kg = 556.127 | USED | PASS
process:pump-sizing | motor_power_kw | 7.5 | kW | inputs from: brief | fertigation_dosing_pump_power_kw = 7.5 | USED | PASS
process:pump-sizing | motor_power_kw | 1.923 | kW | inputs from: brief | drain_transfer_pump_power_kw = 1.923 | USED | PASS
water-storage:buffer-sizing | fresh_water_storage_capacity_m3 | 40 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | fresh_water_storage_capacity_m3 = 40 | USED | PASS
water-storage:buffer-sizing | drain_water_tank_volume_each_m3 | 40 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | drain_water_tank_volume_each_m3 = 40 | USED | PASS
water-storage:buffer-sizing | total_water_storage_volume_m3 | 261.6 | m3 | inputs from: irrigation:ebb-flow-demand, water-treatment-ro:sizing + brief | total_water_storage_volume_m3 = 261.6 | USED | PASS
water-treatment-ro:sizing | ro_membrane_area_m2 | 363.6 | m2 | inputs from: brief | ro_membrane_area_m2 = 363.6 | USED | PASS
water-treatment-ro:sizing | permeate_flow_m3_h | 8 | m3/h | inputs from: brief | ro_permeate_production_m3_per_hr = 8 | USED | PASS
water-treatment-ro:sizing | estimated_capex_gbp | 115727 | GBP | inputs from: brief | estimated_capex_gbp = 115727 | USED | PASS
Worked calculations — every value recomputed live + cross-checked
Arc Flash IEEE 1584 · arc-flash:ieee-1584
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Incident energy (J/cm2 -> cal/cm2) |  |  | incident_energy_cal = incident_energy_j x cal_per_j |  |  |  |  | PASS
incident_energy_j | 3.102 | J/cm2 | [5 empty] | PASS
cal_per_j | 0.23901 | cal/J | [5 empty] | PASS
= result | 0.74138 | cal/cm2 | incident_energy_j x cal_per_j | 0.741 | 0.000378 | cal/cm2 | J/cm2 from the IEEE 1584-2018 empirical model (governing of full/reduced arcing-current cases) | PASS
Control Systems PID Tuning · control-systems:pid-tuning
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
FOPTD time constant (Smith two-point fit) |  |  | tau = 1.5 x (t63 - t28) |  |  |  |  | PASS
t63 | 2.15 | s | [5 empty] | PASS
t28 | 1.06 | s | [5 empty] | PASS
= result | 1.635 | s | 1.5 x (t63 - t28) | 1.635 | 0 | s | Smith's method: 28.3% / 63.2% step-response times of the full plant | PASS
FOPTD dead time |  |  | theta = t63 - tau
t63 | 2.15 | s
tau | 1.635 | s |  |  |  |  | ↳ chained from $B$69
= result | 0.515 | s | t63 - tau | 0.515 | 0 | s | dead time from the same two-point FOPTD fit
Proportional gain (IMC PI rule) |  |  | Kp = (1 / K) x tau / (L + theta)
K | 1
tau | 1.635 | s |  |  |  |  | ↳ chained from $B$69
theta | 0.515 | s |  |  |  |  | ↳ chained from $B$74
L | 5 | s
= result | 0.29646 |  | (1 / K) x tau / (L + theta) | 0.29646 | 1.8858e-07 |  | IMC / Skogestad SIMC rule; L = the IMC lambda time-constant
Integral gain |  |  | Ki = Kp / Ti
Kp | 0.29646 | [5 empty] | ↳ chained from $B$81
Ti | 1.635 | s
= result | 0.18135 | 1/s | Kp / Ti | 0.18132 | 2.1566e-05 | 1/s | integral time Ti = 1.635 s from the IMC rule
Electrical Main Feeder Cable Sizing (BS 7671) · electrical:cable-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
De-rated tabulated-current target |  |  | I_t = I_b / (Ca x Cg) |  |  |  |  | PASS
I_b | 108.25 | A | [5 empty] | PASS
Ca | 1 | [6 empty] | PASS
Cg | 1 | [6 empty] | PASS
= result | 108.25 | A | I_b / (Ca x Cg) | 108.25 | 0 | A | design current basis: design current (given) | PASS
Conductor cross-sectional area (standard selection) |  |  | CSA = smallest standard with ampacity x n_parallel >= I_t
I_t | 108.25 | A |  |  |  |  | ↳ chained from $B$95
n_parallel | 1
= result | 25 | mm2 | smallest standard with ampacity x n_parallel >= I_t | 25 | 0 | mm2 | copper, 90 C thermosetting, Reference Method C (clipped direct)
Volt drop |  |  | Vd = (mV/A/m) x I_b x L / (1000 x n_parallel)
mV/A/m | 1.5 | mV/A/m
I_b | 108.25 | A
L | 50 | m
n_parallel | 1
= result | 8.1188 | V | (mV/A/m) x I_b x L / (1000 x n_parallel) | 8.119 | -0.00025 | V | mV/A/m for 25 mm2 copper (BS 7671 Appendix 4)
Volt drop as percentage of nominal |  |  | Vd_pct = 100 x Vd / U_nom
Vd | 8.1188 | V |  |  |  |  | ↳ chained from $B$107
U_nom | 400 | V
= result | 2.0297 | % | 100 x Vd / U_nom | 2.03 | -0.00025 | % | BS 7671 §525 advisory ceiling 3.0% (within limit)
Electrical Distribution Transformer Sizing · electrical:transformer-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Apparent power demand (informational) |  |  | S_load = P / pf |  |  |  |  | PASS
P | 53 | kW | [5 empty] | PASS
pf | 0.85 | [6 empty] | PASS
= result | 62.3529 | kVA | P / pf | 62.35 | 0.0029412 | kVA | informational only — the nameplate mint below is pf-free (kVA >= kW at any pf) | PASS
Required rating (one-mint incomer rule) |  |  | S_req = P x (1 + headroom)
P | 53 | kW
headroom | 0.25
= result | 66.25 | kVA | P x (1 + headroom) | 66.25 | 0 | kVA | kVA >= load x 1.25 — assumption-free adequacy (kVA >= kW at any power factor)
Transformer nameplate (next standard rating) |  |  | S_rated = ceil_to_standard(S_req)
S_req | 66.25 | kVA |  |  |  |  | ↳ chained from $B$125
= result | 75 | kVA | ceil_to_standard(S_req) | 75 | 0 | kVA | smallest standard preferred kVA rating >= required (IEC 60076 series + the 75 kVA trade step; ladder 25/50/75/100/160/250…)
Primary line current |  |  | I = S x 1000 / (sqrt(3) x U_LL)
S | 75 | kVA
U_LL | 11000 | V
= result | 3.9365 | A | S x 1000 / (sqrt(3) x U_LL) | 3.94 | -0.0035209 | A | three-phase line current (line-to-line voltage)
Secondary line current |  |  | I = S x 1000 / (sqrt(3) x U_LL)
S | 75 | kVA
U_LL | 400 | V
= result | 108.2532 | A | S x 1000 / (sqrt(3) x U_LL) | 108.25 | 0.0031755 | A | three-phase line current (line-to-line voltage)
Liquid Phase GAC Filter Sizing · gac-filter:liquid-phase-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Vessel Volume |  |  | Q * (EBCT / 60) |  |  |  |  | PASS
Q | 14.5 | [6 empty] | PASS
EBCT | 10 | [6 empty] | PASS
= result | 2.4167 | m3 | Q * (EBCT / 60) | 2.4167 | 0 | m3 |  | PASS
Cross-sectional Area |  |  | Q / HLR
Q | 14.5
HLR | 10
= result | 1.45 | m2 | Q / HLR | 1.45 | 0 | m2
Vessel Diameter |  |  | sqrt(4 * A / pi)
A | 1.45
pi | 3.1416 | [5 empty] | ↳ chained from $B$9
= result | 1.3587 | m | sqrt(4 * A / pi) | 1.3587 | -1.5887e-06 | m
Ion Exchange Softener Sizing · ion-exchange:softener-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Hardness Removed |  |  | H_in - H_out |  |  |  |  | PASS
H_in | 15 | [6 empty] | PASS
H_out | 0.1 | [6 empty] | PASS
= result | 14.9 | dH | H_in - H_out | 14.9 | 0 | dH |  | PASS
Hardness Load |  |  | Q * H_removed * EQ_PER_M3_PER_DH * t_regen
Q | 10.7
H_removed | 14.9
EQ_PER_M3_PER_DH | 0.35665
t_regen | 6.5
= result | 369.5946 | eq | Q * H_removed * EQ_PER_M3_PER_DH * t_regen | 369.5946 | 0 | eq
Resin Volume [build-verified] |  |  | Hardness Load / RESIN_CAPACITY
formula |  |  | Hardness Load / RESIN_CAPACITY
substitution |  |  | 369.59 / 1200.0
result | 0.30799 |  |  | 0.308 | -3.8431e-06 | m3 | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)
Vessel Volume [build-verified] |  |  | Resin Volume * VESSEL_FREEBOARD_FACTOR
formula |  |  | Resin Volume * VESSEL_FREEBOARD_FACTOR
substitution |  |  | 0.3080 * 1.5
result | 0.462 |  |  | 0.46199 | 6.7353e-06 | m3 | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)
Salt Consumption [build-verified] |  |  | Resin Volume * SALT_DOSAGE
formula |  |  | Resin Volume * SALT_DOSAGE
substitution |  |  | 0.3080 * 150.0
result | 46.2 |  |  | 46.1993 | 0.00067353 | kg | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)· confirmed = design softener_salt_consumption_max_kg_per_regen
Ebb and Flow Irrigation Demand · irrigation:ebb-flow-demand
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Flood Volume |  |  | Container_Count * Area_per_Container * Flood_Depth |  |  |  |  | PASS
Container_Count | 6000 | [6 empty] | PASS
Area_per_Container | 2 | [6 empty] | PASS
Flood_Depth | 0.05 | [6 empty] | PASS
= result | 600 | m3 | Container_Count * Area_per_Container * Flood_Depth | 600 | 0 | m3 |  | PASS
Peak Irrigation Flow [build-verified] |  |  | Flood Volume / Flood_Time
formula |  |  | Flood Volume / Flood_Time
substitution |  |  | 600.0000 / 0.5
result | 1200 |  |  | 1200 | 0 | m3/h | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)
Drain Collection Sump Volume [build-verified] |  |  | Flood Volume * Drain_Fraction
formula |  |  | Flood Volume * Drain_Fraction
substitution |  |  | 600.0000 * 1.0
result | 600 |  |  | 600 | 0 | m3 | ✓ maths checks out (live: ¦Δ¦ ≤ 2% of the engine value)
Irrigation Pump Sizing · irrigation:pump-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Total system flow |  |  | flow_lpm = (demand_m3_h x 1000) / 60
demand_m3_h | 90 | m3/h | [5 empty] | PASS
= result | 1500 | L/min | (demand_m3_h x 1000) / 60 | 1500 | 0 | L/min | stated peak irrigation demand governs: 90.0 m3/h >= emitter-summed flow 6000 x 2.0 L/h = 12.0 m3/h (pump never undersized vs the demand) | PASS
Total pump head |  |  | head = static_head + friction_head + emitter_head
static_head | 5 | m
friction_head | 2.21 | m
emitter_head | 15.3 | m
= result | 22.51 | m | static_head + friction_head + emitter_head | 22.51 | 0 | m | friction_head from Hazen-Williams (C=150 PVC)
Pump hydraulic power |  |  | P_hyd = 1000 x 9.81 x (Q_m3h / 3600) x head
Q_m3h | 90 | m3/h
head | 22.51 | m |  |  |  |  | ↳ chained from $B$219
= result | 5520.5775 | W | 1000 x 9.81 x (Q_m3h / 3600) x head | 5521.7 | -1.1225 | W | P = rho x g x Q x H, water rho 1000 kg/m3, g 9.81 m/s2
Pump shaft power |  |  | P_shaft = P_hyd / pump_eff
P_hyd | 5520.5775 | W |  |  |  |  | ↳ chained from $B$224
pump_eff | 0.65
= result | 8494.9231 | W | P_hyd / pump_eff | 8495 | -0.076923 | W | drip pump efficiency 0.65 at duty point
Motor input power |  |  | P_motor = P_shaft / motor_eff
P_shaft | 8494.9231 | W |  |  |  |  | ↳ chained from $B$229
motor_eff | 0.88
= result | 9653.4091 | W | P_shaft / motor_eff | 9653.4 | 0.0090909 | W
Pipe velocity |  |  | velocity = (Q_m3h / 3600) / (pipe_area_mm2 / 1000000)
Q_m3h | 90 | m3/h
pipe_area_mm2 | 17671.5 | mm2
= result | 1.4147 | m/s | (Q_m3h / 3600) / (pipe_area_mm2 / 1000000) | 1.415 | -0.0002927 | m/s | keep < 2.5 m/s to avoid erosion / water hammer
Mass Budget Aggregator · mass-aggregator:envelope-check
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Total system mass |  |  | M_total = M_cells + M_transformer + M_pcs + M_racks + M_tare + M_components
M_cells | 0 | kg | [5 empty] | PASS
M_transformer | 500 | kg | [5 empty] | PASS
M_pcs | 0 | kg | [5 empty] | PASS
M_racks | 0 | kg | [5 empty] | PASS
M_tare | 0 | kg | [5 empty] | PASS
M_components | 1000.811 | kg | [5 empty] | PASS
= result | 1500.811 | kg | M_cells + M_transformer + M_pcs + M_racks + M_tare + M_components | 1500.8 | 0.011 | kg | M_racks = rack_count x rack mass each = 0 x 0 kg | PASS
Mass budget utilisation |  |  | U = M_total / M_envelope x 100
M_total | 1500.811 | kg |  |  |  |  | ↳ chained from $B$251
M_envelope |  | kg
= result |  | % | M_total / M_envelope x 100 |  |  | % | brief mass envelope from max_mass_kg_envelope
Mass budget breach (positive = over the envelope) |  |  | B = M_total - M_envelope
M_total | 1500.811 | kg |  |  |  |  | ↳ chained from $B$251
M_envelope |  | kg
= result |  | kg | M_total - M_envelope |  |  | kg
Recommended container count |  |  | N = ceil(M_total / M_envelope)
M_total | 1500.811 | kg |  |  |  |  | ↳ chained from $B$251
M_envelope |  | kg
= result |  |  | ceil(M_total / M_envelope) |  |  |  | round up: any breach forces an additional road-transportable container
Cloth/Screen Filter Sizing · mechanical-filtration:cloth-screen
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Hydraulic Loading Rate |  |  | 4.0 * (micron^0.4) * (20.0 / TSS)^0.5 |  |  |  |  | PASS
micron | 80 | [6 empty] | PASS
TSS | 20 | [6 empty] | PASS
= result | 23.0832 | m/h | 4.0 * (micron^0.4) * (20.0 / TSS)^0.5 | 23.0832 | 0 | m/h |  | PASS
Cloth Filter Area |  |  | Q / HLR
Q | 80
HLR | 23.0832
= result | 3.4657 | m2 | Q / HLR | 3.4657 | 0 | m2
pH Titration Sizing · ph-titration:sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Moles of H+ needed for initial bolus |  |  | mol_H = (buffer_cap / 1000) x delta_pH x volume_l |  |  |  |  | PASS
buffer_cap | 2 | meq/L | [5 empty] | PASS
delta_pH | 1.2 | [6 empty] | PASS
volume_l | 8000 | L | [5 empty] | PASS
= result | 19.2 | mol | (buffer_cap / 1000) x delta_pH x volume_l | 19.2 | 0 | mol | buffer_cap in meq/L; divide by 1000 to convert meq to eq (= mol H+ for monoprotic) | PASS
Initial bolus volume of acid/base |  |  | initial_dose_ml = mol_H / acid_conc x 1000
mol_H | 19.2 | mol |  |  |  |  | ↳ chained from $B$288
acid_conc | 1 | mol/L
= result | 19200 | mL | mol_H / acid_conc x 1000 | 19200 | 0 | mL | Volume = moles / concentration; x 1000 converts L to mL
CO2 production rate in moles per hour |  |  | co2_mol_h = co2_g_h / 44
co2_g_h | 0 | g/h
= result | 0 | mol/h | co2_g_h / 44 | 0 | 0 | mol/h | Molar mass of CO2 = 44 g/mol
H+ generation rate from CO2 dissolution |  |  | H_plus_mol_h = co2_mol_h x 0.30
co2_mol_h | 0 | mol/h |  |  |  |  | ↳ chained from $B$297
= result | 0 | mol/h | co2_mol_h x 0.30 | 0 | 0 | mol/h | ~30% of dissolved CO2 forms H+ in bicarbonate-buffered medium at physiological pH
Uncontrolled pH swing per minute |  |  | dpH_per_min = (H_plus_mol_h / 60 x 1000) / (buffer_cap x volume_l)
H_plus_mol_h | 0 | mol/h |  |  |  |  | ↳ chained from $B$301
buffer_cap | 2 | meq/L
volume_l | 8000 | L
= result | 0 | pH/min | (H_plus_mol_h / 60 x 1000) / (buffer_cap x volume_l) | 0 | 0 | pH/min | H+ rate x 1000 converts mol to mmol (= meq for monoprotic acid)
Pressure Vessel Wall Design (hoop-stress sizing) · pressure-vessel:design
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Internal design pressure |  |  | p_design_mpa = p_design_barg x 0.1 |  |  |  |  | PASS
p_design_barg | 6 | barg | [5 empty] | PASS
= result | 0.6 | MPa | p_design_barg x 0.1 | 0.6 | 0 | MPa | internal gauge design pressure of the process vessel | PASS
Shell minimum thickness (hoop stress, internal pressure) |  |  | t = p_design x D / (2 x S x E - 1.2 x p_design) + corr
p_design | 0.6 | MPa
D | 1358.75 | mm
S | 137 | MPa
E | 0.85
corr | 3 | mm
= result | 6.5113 | mm | p_design x D / (2 x S x E - 1.2 x p_design) + corr | 6.5113 | 4.3484e-06 | mm | ASME VIII Div.1 UG-27 circumferential-stress form (BS EN 13445 equivalent)
Hoop stress at adopted wall (internal pressure) |  |  | sigma_hoop = p_design x D / (2 x t)
p_design | 0.6 | MPa
D | 1358.75 | mm
t | 6.5113 | mm |  |  |  |  | ↳ chained from $B$322
= result | 62.6027 | MPa | p_design x D / (2 x t) | 62.6028 | -9.3935e-05 | MPa | thin-wall cylinder under internal pressure
Yield safety factor (hoop-governing, internal pressure) |  |  | SF_yield = yield_mpa / sigma_hoop
yield_mpa | 290 | MPa
sigma_hoop | 62.6027 | MPa |  |  |  |  | ↳ chained from $B$328
= result | 4.6324 |  | yield_mpa / sigma_hoop | 4.6324 | 6.6029e-07 |  | material steel_316L; yield from datasheet/standard
Cylinder wall mass |  |  | mass = pi x (r_outer^2 - r_inner^2) x length_mm x density / 1e9
r_outer | 685.886 | mm
r_inner | 679.374 | mm
length_mm | 1800 | mm
density | 8000 | kg/m3
= result | 402.2001 | kg | pi x (r_outer^2 - r_inner^2) x length_mm x density / 1e9 | 402.156 | 0.044052 | kg | material steel_316L
Head mass (2 flat-plate heads) |  |  | mass = 2 x pi x r_outer^2 x t x density / 1e9
r_outer | 685.886 | mm
t | 6.5113 | mm |  |  |  |  | ↳ chained from $B$322
density | 8000 | kg/m3
= result | 153.9719 | kg | 2 x pi x r_outer^2 x t x density / 1e9 | 153.971 | 0.0008888 | kg | flat-head approximation (conservative vs torispherical); 2 heads
Total vessel shell mass |  |  | total_mass = mass_cylinder + mass_heads
mass_cylinder | 402.156 | kg
mass_heads | 153.971 | kg
= result | 556.127 | kg | mass_cylinder + mass_heads | 556.127 | 0 | kg
Process Centrifugal Pump Sizing · process:pump-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Per-pump duty flow |  |  | Q_pump = Q_total / N_parallel |  |  |  |  | PASS
Q_total | 45 | m3/h | [5 empty] | PASS
N_parallel | 2 | [6 empty] | PASS
= result | 22.5 | m3/h | Q_total / N_parallel | 22.5 | 0 | m3/h | 2 parallel pump trains share the duty; ONE pump is sized on its share (per-pump x 2 = the loop total) | PASS
Pipe velocity |  |  | V = (Q_m3h / 3600) / (pi/4 x D^2)
Q_m3h | 22.5 | m3/h
D | 0.08 | m
= result | 1.2434 | m/s | (Q_m3h / 3600) / (pi/4 x D^2) | 1.2434 | -2.0071e-06 | m/s | Q_m3h / 3600 converts m3/h to m3/s
Reynolds number |  |  | Re = rho x V x D / mu
rho | 1000 | kg/m3 |  |  |  |  | ↳ chained from $B$6
V | 1.2434 | m/s |  |  |  |  | ↳ chained from $B$364
D | 0.08 | m
mu | 0.001 | Pa.s |  |  |  |  | ↳ chained from $B$10
= result | 99472 |  | rho x V x D / mu | 99471.8 | 0.2 |  | Newtonian fluid; pipe internal bore
Darcy friction factor (Swamee-Jain) |  |  | f = 0.25 / (log10(rel_rough/3.7 + 5.74/Re^0.9))^2
rel_rough | 0.000187
Re | 99472 | [5 empty] | ↳ chained from $B$371
= result | 0.018943 |  | 0.25 / (log10(rel_rough/3.7 + 5.74/Re^0.9))^2 | 0.01895 | -6.5196e-06 |  | Swamee-Jain explicit Colebrook (turbulent)
Pipe friction head (Darcy-Weisbach) |  |  | H_friction = f x (L_eff / D) x V^2 / (2 x g)
f | 0.018943 | [5 empty] | ↳ chained from $B$376
L_eff | 115 | m
D | 0.08 | m
V | 1.2434 | m/s |  |  |  |  | ↳ chained from $B$364
g | 9.8066 | m/s2 |  |  |  |  | ↳ chained from $B$8
= result | 2.153 | m | f x (L_eff / D) x V^2 / (2 x g) | 2.147 | 0.0059539 | m | Darcy-Weisbach pipe friction (chemical-engineering standard)
Process backpressure head |  |  | H_process = backpressure_kpa x 1000 / (rho x g)
backpressure_kpa | 100 | kPa
rho | 1000 | kg/m3 |  |  |  |  | ↳ chained from $B$6
g | 9.8066 | m/s2 |  |  |  |  | ↳ chained from $B$8
= result | 10.1972 | m | backpressure_kpa x 1000 / (rho x g) | 10.197 | 0.00021412 | m | column packing + heat exchangers + filter pressure drop
Pump total dynamic head |  |  | H_total = authoritative TDH (override)
H_total_override | 20 | m
= result | 20 | m | authoritative TDH (override) | 20 | 0 | m | caller-supplied total dynamic head (static+process+friction pre-summed upstream)
Pump hydraulic power |  |  | P_hyd = rho x g x (Q_m3h / 3600) x H_total
rho | 1000 | kg/m3 |  |  |  |  | ↳ chained from $B$6
g | 9.8066 | m/s2 |  |  |  |  | ↳ chained from $B$8
Q_m3h | 22.5 | m3/h
H_total | 20 | m |  |  |  |  | ↳ chained from $B$394
= result | 1225.825 | W | rho x g x (Q_m3h / 3600) x H_total | 1225.8 | 0.025 | W | P = rho g Q H
Pump shaft power |  |  | P_shaft = P_hyd / pump_eff
P_hyd | 1225.825 | W |  |  |  |  | ↳ chained from $B$401
pump_eff | 0.75
= result | 1634.4 | W | P_hyd / pump_eff | 1634.4 | 0 | W | centrifugal pump efficiency 0.75 at duty point
Motor input power |  |  | P_motor = P_shaft / motor_eff
P_shaft | 1634.4 | W |  |  |  |  | ↳ chained from $B$406
motor_eff | 0.85
= result | 1922.8235 | W | P_shaft / motor_eff | 1922.9 | -0.076471 | W | motor efficiency 0.85; recommended frame = 3.0 kW (next standard size with 15% margin)
Water Buffer Tank Sizing · water-storage:buffer-sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Fresh Water Storage |  |  | (irrigation_demand - ro_production) * peak_duration * safety_factor |  |  |  |  | PASS
irrigation_demand | 90 | [6 empty] | PASS
ro_production | 8 | [6 empty] | PASS
peak_duration | 2 | [6 empty] | PASS
safety_factor | 1.2 | [6 empty] | PASS
= result | 196.8 | m3 | (irrigation_demand - ro_production) * peak_duration * safety_factor | 196.8 | 0 | m3 |  | PASS
Total Drain Water Storage |  |  | (irrigation_demand * drain_fraction) * peak_duration * safety_factor
irrigation_demand | 90
drain_fraction | 0.3
peak_duration | 2
safety_factor | 1.2
= result | 64.8 | m3 | (irrigation_demand * drain_fraction) * peak_duration * safety_factor | 64.8 | 0 | m3
Water Treatment RO Sizing · water-treatment-ro:sizing
Calc / input | Value (live) | Unit | Formula (text) | Engine value | Δ | Unit | Assumptions | Cell check
Permeate flow rate |  |  | q_permeate = daily_demand / op_hours |  |  |  |  | PASS
daily_demand | 192000 | L/day | [5 empty] | PASS
op_hours | 24 | h/day | [5 empty] | PASS
= result | 8000 | L/h | daily_demand / op_hours | 8000 | 0 | L/h | system operates at constant flow rate during operating hours | PASS
Feed flow rate (accounting for recovery losses) |  |  | q_feed = q_permeate / recovery
q_permeate | 8000 | L/h |  |  |  |  | ↳ chained from $B$436
recovery | 0.75
= result | 10666.6667 | L/h | q_permeate / recovery | 10666.7 | -0.033333 | L/h | recovery target 75.0% per input
Reject (concentrate) flow rate |  |  | q_reject = q_feed - q_permeate
q_feed | 10666.6667 | L/h |  |  |  |  | ↳ chained from $B$441
q_permeate | 8000 | L/h |  |  |  |  | ↳ chained from $B$436
= result | 2666.7 | L/h | q_feed - q_permeate | 2666.7 | 0 | L/h | mass balance: feed = permeate + reject
Required membrane area |  |  | mem_area = q_permeate / flux_lmh
q_permeate | 8000 | L/h |  |  |  |  | ↳ chained from $B$436
flux_lmh | 22 | L/m2/h
= result | 363.6364 | m2 | q_permeate / flux_lmh | 363.64 | -0.0036364 | m2 | flux 22.0 L/m2/h for bw30_brackish membrane (DOW FILMTEC technical manual)
Hydraulic pump power |  |  | hyd_power = (p_op x q_feed_m3h / 36) / pump_eff
p_op | 12 | bar
q_feed_m3h | 10.6667 | m3/h
pump_eff | 0.7
= result | 5.0794 | kW | (p_op x q_feed_m3h / 36) / pump_eff | 5.0794 | -1.9048e-05 | kW | 1 bar x 1 m3/h / 36 = 0.02778 kW hydraulic (unit conversion)
Specific energy consumption |  |  | energy = hyd_power / (q_permeate / 1000)
hyd_power | 5.0794 | kW |  |  |  |  | ↳ chained from $B$457
q_permeate | 8000 | L/h |  |  |  |  | ↳ chained from $B$436
= result | 0.63492 | kWh/m3 | hyd_power / (q_permeate / 1000) | 0.635 | -7.5e-05 | kWh/m3 | q_permeate converted L/h to m3/h by dividing 1000

## Inputs & Assumptions
Inputs & Assumptions — the economics model drivers |  |  |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · driver integrity (every input driver consumed by a live formula) — drivers referenced by a live formula somewhere 18/18; cell completeness+type contract 54/54 · score = … · full audit: Quality & Audit tab
EVERY yellow cell is editable. Engine-derived values are labelled 'from engine'; market defaults are grounded + cited in Basis. The Economics & Scenarios tabs reference these cells with LIVE formulas — edit one driver and the whole model + every chart recomputes.
Driver | Value | Unit | Basis / source | Cell check
Output volume (output) | 6000 | count | from engine · primary output metric | PASS
Sale price (per output unit) | 0 | £/count | UNVERIFIED — no per-unit market price is derivable for this class. Enter a real sale price to make the economics tabs meaningful; until then revenue / EBITDA / IRR are not valid. | PASS
Consumables price (dosing chemicals · nutrient / fertiliser stock · filter media & membranes) | 0 | £/count | consumable classes derived from the plant's own process/media BoM + contract lines — what it ACTUALLY consumes (not a 'feedstock'); enter a real £ per output unit to price them (0 until priced — meanwhile carried inside 'Other opex') | PASS
Consumable intensity ratio | 0 | ratio | consumable units per output unit (multiplies the consumables price above); 0 until priced | PASS
Energy price | 0.15 | £/kWh | assumed — UK industrial electricity ~£0.15/kWh (edit to your tariff) | PASS
Connected electrical load | 53 | kW | from engine · connected_electrical_load_kw | PASS
Electrical load factor | 0.65 | avg/peak | assumed average/peak electrical load factor — supply a class duty-cycle to refine | PASS
Operating hours | 8000 | h/yr | assumed — typical process-plant annual operating hours (supply a class duty-cycle to refine) | PASS
Design process flow (peak) | 90 | m³/h | from engine · largest process-flow quantity (the PEAK simultaneous demand); the Financial model's annual-delivered-volume divisor references this cell LIVE — edit it and the levelised £/m³ recomputes | PASS
Water utilisation (delivered ÷ design flow) | 0.25 | fraction | multiplies the design flow above · assumed — the design flow is the PEAK simultaneous demand, so annual delivered volume = design flow × 8760 h × this factor. 0.25 models an intermittent, demand-driven duty (sequenced valve sections / batch draw-off deliver ≈25% of the peak run continuously); set ≈0.9 for a continuous process duty, or edit to metered annual demand ÷ (design flow × 8760). Drives the levelised £/m³ on the Financial model — the electrical load factor above sizes the ENERGY line only. | PASS
Labour | 25000 | £/yr | assumed — supply a real figure. No operating headcount signal, so this is defaulted as an UNMANNED / skid plant: ~£25,000/yr for remote monitoring + periodic maintenance visits (NOT a % of capex). Enter your real annual labour cost, or supply an operating headcount. | PASS
Maintenance | 3 | % capex/yr | process-plant norm | PASS
Other opex | 27502 | £/yr | assumed — 2% of installed capex/yr (consumables, insurance, overhead; supply a class opex model to refine) | PASS
Installed capex | 1375105 | £ | from engine · costStack.installed_asp_gbp (BoM + assembly + install) | PASS
Scaling exponent n (capex ∝ output^n) | 1 | n | 1.0 = LINEAR — a MODULAR plant scaled by replicating identical units (more tanks/pumps/skids); capex per output unit is constant, de-risked + testable at small scale (the Fractional Forge default for modular plant). 0.6 = the six-tenths law for MONOLITHIC equipment that scales by getting bigger. Edit to model either regime — every capex/economics cell on the sweep + solver recomputes live off this. | PASS
Discount rate | 10 | % | real WACC for a small infrastructure project | PASS
Investor hurdle rate (IRR) | 15 | % | the minimum IRR an investor demands before deploying capital — the 'investable' bar on the Investment Analysis tab; edit to your fund's threshold | PASS
Project life | 20 | yr | asset economic life for the NPV horizon | PASS

## Part names
Part names — the master list |  |  |  | ↑ Contents
⬤ TAB QUALITY 8/10 · PASS (target ≥8, live from the Quality & Audit score cell) · dedupe + completeness (every BoM tag present exactly once) — part tags unique (each physical thing named once) 107/107; cell completeness+type contract 391/392 · score =… · full audit: Quality & Audit tab
THE single source of every part's name. Each name is typed ONCE here; every other tab (BoM, Cost, Spec sheets, Connection trace, schedules) REFERENCES these cells, never repeats the string — edit a name here and it updates across the whole workbook. Select a Name cell and use Formulas ▸ Trace Dependents to see everywhere it is used. One row per principal part; sub-components are listed under their parent on the BoM.
Tag | Name | Qty | Requirement (as stated) | Cell check
X-147 | 3 Part Union Fittings | 1 | 3 Part Union Fittings | PASS
D-101 | 3 Phase Power Input | 1 | 3 Phase Power Input | PASS
X-130 | Automated Ball Valves | 1 | Automated Ball Valves | PASS
X-149 | Cable Glands | 1 | Cable Glands | PASS
X-142 | Cable Trays | 1 | Cable Trays | PASS
X-112 / V-111 | Check Valve | 2 | Check Valve · MERGED ROWS (singular/plural): 'Check Valves' (X-112) + 'Check Valve' (V-111) | PASS
I-109 | Chlorine Sensor | 1 | Chlorine Sensor | PASS
X-101 | Cip System | 1 | Cip System | PASS
X-146 | Cip System Connections | 1 | Cip System Connections | PASS
TK-102 / TK-101 | Cip Tank | 2 | Cip Tank · 1.4 m dia x 1.3 m · MERGED ROWS (synonym): 'Cleaning Tank' (TK-102) + 'Cip Tank' (TK-101) | PASS
X-106 / X-110 | Circuit Breaker | 2 | Circuit Breaker · MERGED ROWS (singular/plural): 'Circuit Breakers' (X-106) + 'Circuit Breaker' (X-110) | PASS
V-103 | Cloth Filter | 2 | Cloth Filter · 80 m³/h · 3 m² area | PASS
X-114 | Compartment Spacers | 1 | Compartment Spacers | PASS
X-103 | Concentrate Outlet | 1 | Concentrate Outlet | PASS
I-104 | Conductivity Sensor | 1 | Conductivity Sensor | PASS
U-201 | Control + Instrument UPS | 1 | Control + Instrument UPS · 5 kW (30 min) · 600x510x660 mm | PASS
X-109 | DC Power Cabling | 1 | DC Power Cabling | PASS
X-120 | Dc3 Power Controller | 1 | Dc3 Power Controller | PASS
I-103 | Digital Control Panel | 1 | Digital Control Panel | PASS
M-101 | Distribution Manifold | 2 | Distribution Manifold · 45 m³/h · 700x595x770 mm | PASS
TK-114 | Drain Collection Sump | 2 | Drain Collection Sump · 2.1 m dia x 1.4 m | PASS
P-104 | Drain Transfer Pump | 2 | Drain Transfer Pump · 2 kW · 600x510x660 mm | PASS
TK-106 | Drain Water Tank | 2 | Drain Water Tank · 3.7 m dia x 3.7 m | PASS
I-102 | Electrical Control Cabinet | 1 | Electrical Control Cabinet | PASS
X-105 | Electrical Control Panel | 1 | Electrical Control Panel | PASS
X-141 / X-144 / I-114 | Emergency Stop | 3 | Emergency Stop · MERGED ROWS (synonym): 'Emergency Stop Button' (X-141) + 'Emergency Stop' (X-144) + 'Emergency Stop Switch' (I-114) | PASS
X-118 | Ethernet Ip Module | 1 | Ethernet Ip Module | PASS
P-106 | Fertigation Dosing Pump | 2 | Fertigation Dosing Pump · 8 kW · 600x510x660 mm | PASS
X-139 | Flexmount Connectors | 1 | Flexmount Connectors | PASS
X-128 | Flow Control Valves | 1 | Flow Control Valves | PASS
I-105 / X-131 | Flow Meter | 2 | Flow Meter · MERGED ROWS (singular/plural): 'Flow Meter' (I-105) + 'Flow Meters' (X-131) | PASS
TK-108 | Fresh Water Tank | 1 | Fresh Water Tank · 3.7 m dia x 3.7 m | PASS
V-101 | Gac Filter | 1 | Gac Filter · 1.3 m dia x 1.4 m | PASS
V-105 | Gac Softener | 1 | Gac Softener · 15 m³/h · 0.9 m dia x 1.8 m | PASS
F-3 | Grp Membrane Housings | 1 | Grp Membrane Housings · 364 m² area | PASS
P-102 | Hand Watering Pump | 1 | Hand Watering Pump · 25 m³/h · 900x500x700 mm | PASS
X-157 | Hand watering — ring main to both departments | 428 | Hand watering — ring main to both departments · DN90 PVC-U · 428 m | PASS
I-112 | High Pressure Switch | 1 | High Pressure Switch | PASS
X-121 | HMI Touchscreen | 1 | HMI Touchscreen | PASS
X-119 | Hoogendoorn iSii Remote Monitoring | 1 | Hoogendoorn iSii Remote Monitoring | PASS
X-113 | Hydraulic Connectors | 1 | Hydraulic Connectors | PASS
FCV-201–202 | Inlet Flow Control Valve | 2 | Inlet Flow Control Valve · 45 m³/h · DN100 modulating control valve (45 m³/h @ 2 m/s) | PASS
P-103 | Irrigation Pump | 1 | Irrigation Pump · 90 m³/h · 1379x766x1073 mm | PASS
X-150 | Isolation Valves | 1 | Isolation Valves | PASS
I-113 | Leak Detection Sensor | 1 | Leak Detection Sensor | PASS
LT-201–213 | Level Transmitter | 13 | Level Transmitter · 0–1.4 m | PASS
X-137 | Leveling Feet | 1 | Leveling Feet | PASS
I-111 | Low Pressure Switch | 1 | Low Pressure Switch | PASS
EP-101 | Main Switchboard | 1 | Main Switchboard · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | PASS
EP-102 | Mains Incomer | 1 | Mains Incomer · 125 A · 400 V 3-phase LV incomer · 125 A ACB frame (sized to 53 kW connected load, PF 0.9, 25% margin) | PASS
V-108 / X-129 | Manual Ball Valve | 2 | Manual Ball Valve · MERGED ROWS (singular/plural): 'Manual Ball Valve' (V-108) + 'Manual Ball Valves' (X-129) | PASS
X-127 | Manual Isolation Valves | 1 | Manual Isolation Valves | PASS
X-117 | Modbus Interface | 1 | Modbus Interface | PASS
X-123 | Modbus Tcp Interface | 1 | Modbus Tcp Interface | PASS
X-148 | Modular Stack Design | 1 | Modular Stack Design | PASS
X-138 | Module Support System | 1 | Module Support System | PASS
EP-104 | Motor Control Center | 1 | Motor Control Center | PASS
X-145 | Motor Overload Protection | 1 | Motor Overload Protection | PASS
X-107 | Motor Starter | 1 | Motor Starter | PASS
TK-103 | Nutrient Tank | 8 | Nutrient Tank · 1.1 m dia x 1.1 m | PASS
I-107 | Orp Sensor | 1 | Orp Sensor | PASS
X-143 | Overcurrent Protection | 1 | Overcurrent Protection | PASS
X-140 | Painted Carbon Steel Skid Frame | 1 | Painted Carbon Steel Skid Frame · 2.3 m dia x 2.4 m | PASS
X-135 | Painted Steel Skid Frame | 1 | Painted Steel Skid Frame · 2.3 m dia x 2.4 m | PASS
X-104 | Permeate Outlet | 1 | Permeate Outlet | PASS
AT-201 | pH Analyser | 1 | pH Analyser · pH 0–14 (control 0.3) | PASS
I-106 | Ph Sensor | 1 | Ph Sensor | PASS
X-102 | Piping Network | 1 | Piping Network | PASS
X-115 / X-122 | PLC Controller | 2 | PLC Controller · MERGED ROWS (synonym): 'PLC Controller' (X-115) + 'Siemens S7 1200 PLC' (X-122) | PASS
X-126 | Pneumatic Actuated Valves | 200 | Pneumatic Actuated Valves | PASS
— | Pneumatic Actuators | 200 | Pneumatic Actuators | ⚠ FAIL — 'Tag' placeholder '—'
V-109 | Pneumatic Control Valve | 1 | Pneumatic Control Valve | PASS
X-132 | Power Supply Unit | 1 | Power Supply Unit | PASS
V-110 | Pressure Relief Valve | 1 | Pressure Relief Valve · 4 kW · 600x510x660 mm | PASS
PT-201–217 | Pressure Transmitter | 17 | Pressure Transmitter · 0–5 bar | PASS
X-124 | Remote Monitoring Gateway | 1 | Remote Monitoring Gateway | PASS
Z-101 | Reverse Osmosis Skid | 1 | Reverse Osmosis Skid · 2.3 m dia x 2.4 m | PASS
P-101 | Ro High Pressure Pump | 1 | Ro High Pressure Pump · 4 kW · 600x510x660 mm | PASS
F-1 | Ro Membrane Elements | 1 | Ro Membrane Elements · 364 m² area | PASS
X-134 | Sample Valves | 1 | Sample Valves | PASS
EP-103 | SCADA / Plant Control System | 1 | SCADA / Plant Control System · 53 kW plant | PASS
I-108 | Silica Analyzer | 1 | Silica Analyzer | PASS
V-106 | Softener Vessel | 2 | Softener Vessel · 1.2 m dia x 1.3 m | PASS
X-125 / V-107 | Solenoid Valve | 2 | Solenoid Valve · MERGED ROWS (singular/plural): 'Solenoid Valves' (X-125) + 'Solenoid Valve' (V-107) | PASS
X-136 | Sst304 Skid Frame | 1 | Sst304 Skid Frame · 2.3 m dia x 2.4 m | PASS
G-201 | Standby Diesel Generator | 1 | Standby Diesel Generator · 60 kVA · 862x733x948 mm | PASS
X-133 | Surge Protection Device | 1 | Surge Protection Device | PASS
I-110 | Tds Sensor | 1 | Tds Sensor | PASS
X-108 / X-111 | Terminal Block | 2 | Terminal Block · MERGED ROWS (singular/plural): 'Terminal Blocks' (X-108) + 'Terminal Block' (X-111) | PASS
TX-101 | Transformer | 1 | Transformer · 75 kW · 1090x927x1199 mm | PASS
F-2 | Uf Membrane Bank | 1 | Uf Membrane Bank · 364 m² area | PASS
Z-102 | Uf Module Bank | 1 | Uf Module Bank | PASS
Z-103 | Ultrafiltration Module | 1 | Ultrafiltration Module | PASS
V-102 | Uv Disinfection | 1 | Uv Disinfection · 4 kW · 600x510x660 mm | PASS
X-116 | Veolia Ro40 Controller | 1 | Veolia Ro40 Controller | PASS
INV-2 | Vfd Controller | 1 | Vfd Controller | PASS
INV-1 | Vfd Drive | 1 | Vfd Drive | PASS
X-151 | Zoned distribution — department delivery mains | 214 | Zoned distribution — department delivery mains · DN125 PVC-U · 214 m | PASS

## Glossary
Glossary — abbreviations & symbols |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · glossary contract (every term defined + no orphan terms) — every rendered term carries a definition 47/47; terms actually used somewhere in the workbook 47/47 · score = … · full audit: Quality & Audit tab
Plain-English meaning of every abbreviation used on the schedule, drawing, bill-of-materials and cost tabs. Standard engineering nomenclature (British spelling); the same reference applies to any plant.
Pipe sizes & materials
DN | Diameter Nominal — the nominal bore size of a pipe / valve in millimetres (e.g. DN200 ≈ 200 mm bore). A size label, not the exact internal diameter.
316L | 316L stainless steel — low-carbon austenitic stainless; the corrosion-resistant grade for process-water, oxidiser and hygienic duties.
304 / 304L | 304 / 304L stainless steel — general-purpose austenitic stainless.
DUPLEX | Duplex stainless steel — high-strength, chloride-corrosion-resistant stainless for seawater / brackish duties.
HDPE / PE100 | High-density polyethylene (PE100 grade) — tough, corrosion-free thermoplastic pipe for water / effluent at low pressure.
FRP / GRP | Fibre-reinforced plastic (glass-reinforced plastic) — moulded composite for tanks and vessels.
PVC / uPVC | Poly(vinyl chloride) pipe grades — low-cost drainage / cold-water pipe.
Instrumentation (ISA tags)
ISA | The instrument-tag convention to ISA-5.1 (International Society of Automation) — the letter code naming what an instrument measures and does.
LT | Level Transmitter — measures liquid level.
PT | Pressure Transmitter — measures pressure.
FT | Flow Transmitter — measures flow rate.
AT | Analyser Transmitter — measures a composition variable, e.g. dissolved oxygen, pH or redox.
AT (pH) / AT (ORP) | Analyser variant: pH, or oxidation-reduction (redox) potential.
4–20 mA | The standard analogue field-signal current loop (4 mA = zero, 20 mA = full scale).
PLC / SCADA | Programmable Logic Controller / Supervisory Control And Data Acquisition — the plant control system.
Equipment & package tags
P (tag) | Pump — equipment-tag letter (P-101, P-102 …).
TK (tag) | Tank — bulk liquid storage vessel (TK-101 …).
V (tag) | Vessel — pressure / process vessel, guard bed, filter housing (V-101 …).
D (tag) | Drum / separator — knock-out drum, decanter, three-phase separator (D-101 …). The tag scheme's separator letter.
U (tag) | Utility / package unit — a balance-of-plant utility supplied as one packaged item, e.g. an uninterruptible power supply (U-201 …).
Z (tag) | Packaged skid unit — a vendor skid delivered as one assembly, e.g. a reverse-osmosis or ultrafiltration skid (Z-101 …). Distinct from the HVAC zone identifiers Z-01, Z-02 … (see the HVAC group).
EP (tag) | Electrical panel — switchgear, motor-control-centre or control cabinet (EP-101 …).
X (tag) | General / unclassified equipment block (X-101 …).
C (tag) | Column / tower (C-101 …); on the bill of materials a C-numbered row (C01, C02 …) is a CONNECTION line — an interconnecting pipe or cable run.
I (tag) | Field instrument or in-line device (I-101 …).
Valves & safety
FC | Fail Closed — the valve drives to the CLOSED position on loss of signal, air or power.
PSV / PRV | Pressure Safety / Relief Valve — mechanical over-pressure protection.
XV / SDV | Shutdown / emergency-shutdown Valve — fast on/off safety isolation.
PCV | Pressure / Process Control Valve — a modulating control valve.
HV | Hand Valve — manual isolation.
NRV / CV | Non-Return Valve / Check Valve — prevents reverse flow.
Electrical
MCB | Miniature Circuit Breaker.
UPS | Uninterruptible Power Supply — battery-backed supply for control / instruments.
VSD / VFD | Variable-Speed / Variable-Frequency Drive — controls motor speed.
LV / HV | Low Voltage / High Voltage.
ΔU % | Volt-drop percentage — the voltage lost along a cable run as a fraction of the supply voltage (kept within spec, typically ≤ 5 %).
HVAC
HVAC | Heating, Ventilation & Air-Conditioning.
Bill-of-materials status codes
BESPOKE | Made-to-order item — fabricated / engineered to spec; no off-the-shelf part number.
UTILITY | A utility / commodity item (pipework, cable, civils) priced parametrically.
SYSTEM | A multi-part packaged system priced as one unit.
INSTRUMENT | A field-instrument line.
Units
m³/h | Cubic metres per hour — volumetric flow.
m³/s | Cubic metres per second — volumetric flow.
kW / kWh | Kilowatt (power) / kilowatt-hour (energy).
mg/L | Milligrams per litre — concentration (e.g. dissolved oxygen).
bar / barg | Pressure / pressure gauge (above atmospheric).
t/yr | Tonnes per year — annual throughput.

## Audit data
Audit data — the embedded operands behind the live verdict formulas |  |  |  |  | ↑ Contents
⬤ TAB QUALITY 10/10 · PASS (target ≥8, live from the Quality & Audit score cell) · audit-operand register contract (every embedded operand carries its label + provenance; per-row Cell check formulas) — cell completeness+type contract 100/100 · score = … · full audit: Quality & Audit tab
Every check in this workbook is a LIVE formula. Where a check compares against data that lives outside the workbook (the single-line drawing, the engineering contract, a build-time classification), the compared value is EMBEDDED here with its provenance — so the workbook contains everything its own verdicts depend on, and the formula bar on any verdict cell shows exactly which operands it judges.
# | Group | Operand | Value | Provenance (where this value comes from) | Cell check
1 | Sense-check | all-in cost — LLM verdict | ok | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
2 | Sense-check | output — irrigation_demand — LLM verdict | warn | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
3 | Sense-check | output — ro_permeate_capacity — LLM verdict | ok | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
4 | Sense-check | output — water_storage_capacity — LLM verdict | ok | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
5 | Sense-check | output — actuated_valves — LLM verdict | ok | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
6 | Sense-check | output — ro_recovery — LLM verdict | ok | benchmarkDivergence.findings[].verdict (scripts/lib/benchmark-expectation.ts) | PASS
7 | Electrical | volt-drop limit (%) | 5 | the schedule's published ≤5% volt-drop band (BS 7671 §525 practice) | PASS
8 | Electrical | MAIN DISTRIBUTION BOARD (TP&N) — system voltage (V) | 400 | panel-schedule.md '## MAIN DISTRIBUTION BOARD (TP&N)' System field | PASS
9 | Electrical | MAIN DISTRIBUTION BOARD (TP&N) — pf·η denominator factor | 1.7321 | √3 for a 3-phase board, 1 for DC / single-phase (from the board's own System field) | PASS
10 | Electrical | Main Switchboard — system voltage (V) | 400 | panel-schedule.md '## Main Switchboard' System field | PASS
11 | Electrical | Main Switchboard — pf·η denominator factor | 1.7321 | √3 for a 3-phase board, 1 for DC / single-phase (from the board's own System field) | PASS
12 | Electrical · reconciliation | MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] — Σ-current/busbar ratio | 1 | the schedule's own printed reconciliation line | PASS
13 | Electrical · reconciliation | MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] — schedule's own verdict | OK | the schedule's printed OK/REVIEW verdict | PASS
14 | Electrical · reconciliation | MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] — busbar rating | 100 A | panel-schedule.md board Field/Value table | PASS
15 | Electrical · reconciliation | MAIN DISTRIBUTION BOARD (TP&N) · [board reconciliation] — evidence |  | build-computed reconciliation reasons ('' = clean) | PASS
16 | Electrical · reconciliation | Main Switchboard · [board reconciliation] — Σ-current/busbar ratio | 1 | the schedule's own printed reconciliation line | PASS
17 | Electrical · reconciliation | Main Switchboard · [board reconciliation] — schedule's own verdict | OK | the schedule's printed OK/REVIEW verdict | PASS
18 | Electrical · reconciliation | Main Switchboard · [board reconciliation] — busbar rating | 20 A | panel-schedule.md board Field/Value table | PASS
19 | Electrical · reconciliation | Main Switchboard · [board reconciliation] — evidence |  | build-computed reconciliation reasons ('' = clean) | PASS
20 | Electrical · reconciliation | system voltage (V) — SCHEDULE | 400 | panel-schedule.md system line | PASS
21 | Electrical · reconciliation | voltage tokens — DRAWING | 400 | every 'N V' token on the single-line drawing | PASS
22 | Electrical · reconciliation | schedule boards ABSENT from the single-line drawing | MAIN DISTRIBUTION BOARD (TP&N) | panel-schedule.md board headings not found in the single-line-diagram.svg text (computed at build; '' = every board found) | PASS
23 | Electrical · reconciliation | schedule boards (named) | MAIN DISTRIBUTION BOARD (TP&N), Main Switchboard | panel-schedule.md '## <board>' headings | PASS
24 | Electrical · reconciliation | transformer rating (kVA) — DRAWING | 75 | read from drawings/single-line-diagram.svg (TX label text) | PASS
25 | Electrical · reconciliation | transformer rating (kVA) — CONTRACT | 75 | orchestratorContract.quantities transformer_kva / main_transformer_kva / transformer_rating_kva | PASS